## Overview
CERS UST Facility/Tank Data Download
This spreadsheet contains UST Facility, Tank, Monitoring Plan, and Certification of Installation/Modification data exported from the California Environmental Reporting System (CERS). Use Excel's worksheet tabs or the hyperlinks below to access the export data. Please note, this exported data only includes data that has been "Accepted" by Regulators. Any UST Facility data that has been "Submitted" but has never been "Accepted" by a Regulator is not shown.
Tank counts:
• | The ‘UST Facility Info’ table (the first generated worksheet) Field 404, ‘Total Number of USTs’, provides a count of all active tanks listed in the last accepted submittal shown on that table. It may not be equal to the next worksheet ‘UST Tank and Monitoring Plan Info Count of Exported Records’ shown on this page. The UST Tank and Monitoring Plan Info is a count of all tanks reported on all accepted submittals. In some cases, such as if a tank ID is altered or a business user reports additional tanks on a submittal, there will be tanks reported on one submittal and not on another. The ‘UST Tank and Monitoring Plan Info Count of Exported Records’ includes all such tanks.
• | Date Range vs No Date Range:
| o | Tanks reported in CERS that do not have a tank install date will be reported if no date range is selected. They will not be reported if a date range is selected.
| o | UPA staff are encouraged to ensure that all active tanks have a tank installation date and that all permanently closed or removed tanks have a tank closure date.
• | Report 6: This report will report all tanks and therefore should be consistent with ‘UST Tank and Monitoring Plan Info Count of Exported Records’. The date range limitations are also the same, tank records with no date installed or closed will not be counted if the report is run with a date range.
Data Export Date/Time: |  |  | 8/14/2024 3:44:00 PM
Record Filtering Criteria (if any): |  |  | Facility regulated by "Marin County Dept of Public Works CUPA".
Generated Worksheets |  |  | Count of Exported Records
UST Facility Info |  |  | 98
UST Tank & Monitoring Plan Info |  |  | 259
UST Cert of Installation & Mod |  |  | 0
For more information about the meaning of the Unified Program Data Dictionary (UPDD) codes, visit the CUPA Data Registry at the following URL:
https://cersapps.calepa.ca.gov/DataRegistry

## UST Facility Info
Facility Identification and Location | [9 empty] | General UST Facility Permit Info | [6 empty] | Property Owner | [6 empty] | Tank Owner | [7 empty] | Tank Operator | [6 empty] | Petroleum UST Financial Responsibility Mechanism(s) | [10 empty] | Certification / Applicant Information |  |  |  | Submittal / Acceptance Information |  |  |  | Regulator Information
1a | 1 |  |  | 3 | 103 | 104 |  |  |  | 400 | 403 | 421 | 423 | 404 | 405 | 406 | 407 | 408 | 409 | 410 | 411 | 412 | 412a | 414 | 415 | 416 | 417 | 418 | 419 | 419a | 420 | 428-1 | 428-2 | 428-3 | 428-4 | 428-5 | 428-6 | 428-7 | 422-1 | 422-2 | 422-3 | 422-4 | 422-5 | 422-6 | 422-8 | 422-9 | 422-10 | 422-99 | 422-99a | 424 | 426 | 427 | 425
CERS ID | Facility ID | Organization Name | Organization Code | Facility Name | Facility Street Address | Facility City | Facility ZIP Code | Latitude Measure | Longitude Measure | Type of Action | UST Facility Type | BOE Number | Permit Holder Notification Information | Total Number of USTs | Indian or Trust Land | Supervisor of Division, Section, or Office | Name | Phone | Mailing Address | City | State | ZIP Code | Country | Name | Phone | Mailing Address | City | State | ZIP Code | Country | Type | Name | Phone | Mailing Address | City | State | ZIP Code | Country | Self- Insured | Guarantee | Insurance | Surety Bond | Letter of Credit | Exemption | State Fund and CFO letter | State Fund and CD | Local Government Mechanism | Other | Other Description | Date Certified | Applicant Name | Applicant Title | Applicant Phone | Date Submitted to CERS | Date Accepted by Regulator | Regulator Comment | Regulator Agent Name | Regulator Name | Regulator Type
10030615 | 21-000-601316 | AS Convenience & Energy Inc. | 90379039 | 24/7 Northgate | 930 Del Presidio Boulevard | San Rafael | 94903 | 38.0066 | -122.5442 | Confirmed/Updated Information | Motor Vehicle Fueling | 245092896 | Tank Owner | 4 | Yes |  | 930 Del Presidio Blvd LLC | (415) 710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | 930 Del Presidio Blvd LLC | (415) 710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | AS Convenience & Energy Inc. | (415) 710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2024-04-19 09:25 | 2024-04-19 13:15 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | 38.0072 | -122.5443 | Confirmed/Updated Information | Motor Vehicle Fueling | 44031913 | Tank Owner | 3 | No |  | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | Non-Government | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | No | No | No | No | Yes | No | No | No | No | No |  |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | 925-842-9002 | 2024-05-13 13:20 | 2024-05-15 13:57 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030663 | 21-000-601496 | Matt and Jeff's Fuel 24:7 | 90838336 | Matt and Jeff's Fuel 24:7 | 1515 Second Street | San Rafael | 94901 | 37.9716 | -122.5343 | New Permit | Motor Vehicle Fueling | 44041172 | Tank Owner | 3 | No |  | Petroleum Sales, Inc. | 4152561600 | 1475 Second Street | San Rafael | CA | 94901 | United States | Petroleum Sales, Inc. | 4152561600 | 1475 Second Street | San Rafael | CA | 94901 | United States | Non-Government | Matt and Jeff's Fuel 24:7 | 4157217886 | 1515 Second Street | San Rafael | CA | 94901 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-03-07 15:26 | 2023-03-13 12:06 | Field Verified 3/6 during inspection and assisting facility with submittal | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030669 | 21-000-601222 | Faizan Corporation | 90427900 | Faizan Corporation | 170 Merrydale Road | San Rafael | 94903 | 37.9956 | -122.5344 | Confirmed/Updated Information | Motor Vehicle Fueling | 044049106 | Facility Operator | 3 | No |  | Faizan Corporation | 510- 862-3333 | 170 Merrydale Road | San Rafael | CA | 94903 | United States | Faizan Corporation | (510) 862-3333 | 170 Merrydale Road | San Rafael | CA | 94903 | United States | Non-Government | Faizan Corporation | 510-862-3333 | 170 Merrydale Road | San Rafael | CA | 94903 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Haji Alam | President | (510) 862-3333 | 2024-04-22 17:57 | 2024-04-24 10:19 |  | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030819 | 21-000-300104 | Marin Sanitary Service | 90097396 | Marin Sanitary Service | 1050 Andersen Drive | San Rafael | 94901 | 37.9548 | -122.5046 | Confirmed/Updated Information | Motor Vehicle Fueling | 44013904 | Facility Owner | 2 | No |  | Marin Sanitary Service | (415) 456-2601 | 1050 Andersen Drive | San Rafael | CA | 94901 | United States | Marin Sanitary Service | (415) 456-2601 | 1050 Andersen Drive | San Rafael | CA | 94901 | United States | Non-Government | Marin Sanitary Service | (415) 456-2601 | 1050 Andersen Drive | San Rafael | CA | 94901 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Joseph Garbarino | vice president | (415)456-2601 | 2023-01-10 11:38 | 2023-01-31 22:27 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10030891 | 21-000-300133 | Union 76 Of Marin | 90852535 | Union 76 Of Marin | 831 Francisco Boulevard East | San Rafael | 94901 | 37.9625 | -122.5088 | Confirmed/Updated Information | Motor Vehicle Fueling | 44381331 | Facility Owner | 3 | No |  | PETER JIZRAWI | 4155697939 | 831 FRANCISCO BLVD. EAST | SAN RAFAEL | CA | 94901 | United States | PETER JIZRAWI | 4155697939 | 831 FRANCISCO BLVD. EAST | SAN RAFAEL | CA | 94901 | United States | Non-Government | Geoge Antar | 4155331925 | 831 FRANCISCO BLVD. EAST | SAN RAFAEL | CA | 94901 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | PETER JIZRAWI | OWNER | 415-457-4272 | 2024-01-04 10:57 | 2024-01-04 12:19 | field verified at annual monitoring certification 12.12.2023 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030894 | 21-000-300134 | Peter's Beacon | 90097696 | Peter's Beacon | 108 Bellam Boulevard | San Rafael | 94901 | 37.9604 | -122.5043 | Renewal Permit | Motor Vehicle Fueling | 4401377 | Facility Operator | 3 | No |  | Peter Jizrawi | 415-457-3020 | P. O. Box 9152 | San Rafael | CA | 94912 | United States | Peter Jizrawi | 415-457-3020 | P. O. Box 9152 | San Rafael | CA | 94912 | United States | Non-Government | Samir Jizrawi | 415-286-1293 | 108 Bellam Blvd | San Rafael | Ca | 94901 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Samir Jizrawi | Owner | 415-457-3020 | 2023-05-12 13:12 | 2023-09-14 11:07 |  | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031020 | 21-000-300178 | Central Marin Sanitation Agency | 90098158 | Central Marin Sanitation Agency | 1301 Andersen Drive | San Rafael | 94901 | 37.9485 | -122.4953 | Confirmed/Updated Information | Other | 44013842 | Facility Owner | 2 | No |  | Central Marin Sanitation Agency | 415-459-1455 | 1301 Anderson Dr | San Rafael | CA | 94901 | United States | Central Marin Sanitation Agency | 415-459-1455 | 1301 Anderson Dr | San Rafael | CA | 94901 | United States | Local Agency/District | Central Marin Sanitation Agency | 415-459-1455 | 1301 Anderson Dr | San Rafael | CA | 94901 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Mary Jo Ramey | Environmental Services Analyst | (415) 459-1455 ext140 | 2023-12-01 06:23 | 2023-12-27 10:12 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031029 | 21-000-300181 | Kaiser Permanente Medical Center | 90098194 | Kaiser Permanente San Rafael Medical Center | 99 Montecillo Road | San Rafael | 94903 | 38.004 | -122.5553 | Confirmed/Updated Information | Other | 044000692 | Tank Operator | 1 | No |  | KAISER FOUNDATION HOSPITALS | 510-271-5800 | ONE KAISER PLAZA | OAKLAND | CA | 94612 | United States | KAISER FOUNDATION HOSPITALS | 510-271-5800 | ONE KAISER PLAZA | OAKLAND | CA | 94612 | United States | Non-Government | KAISER PERMANENTE SAN RAFAEL MEDICAL CENTER | 415-444-2000 | 99 MONTECILLO RD | SAN RAFAEL | CA | 94903 | United States | Yes | No | No | No | No | No | No | No | No | No |  |  | RICHARD NEWTON | CHIEF ENGINEER | 415-444-2135 | 2024-04-10 15:09 | 2024-06-07 12:35 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031032 | 21-000-300182 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 06157 | 1401 2nd St | San Rafael | 94901 | 37.9714 | -122.5325 | Confirmed/Updated Information | Motor Vehicle Fueling | 228240256 | Tank Owner | 4 | No |  | BP PRODUCTS NORTH AMERICA, INC. | 530-777-8942 | PO BOX 6038 | ARTESIA | CA | 90702 | United States | BP PRODUCTS NORTH AMERICA, INC. | 530-777-8942 | PO BOX 6038 | ARTESIA | CA | 90702 | United States | Non-Government | SAN RAFAEL SMOG TEST & REPAIR STATION | (415) 456-9575 | 1401 2ND STREET | SAN RAFAEL | CA | 94901 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | 312-809-4230 | 2024-07-01 15:54 | 2024-07-10 12:13 | Field verified 07.02.2024 during annual monitoring certification | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031083 | 21-000-300200 | PG&E | 90000226 | PG&E - San Rafael Service Center | 1220 Andersen Drive | San Rafael | 94901 | 37.9511 | -122.4994 | Permanent Facility Closure | Motor Vehicle Fueling | 44002884 | Tank Operator | 0 | No |  | PG&E | 415-973-7204 | 77 Beale Street | San Francisco | CA | 94105 | United States | PG&E - Attn: Environmental Mgmt | 415-973-7204 | 77 Beale Street | San Francisco | CA | 94105 | United States | Non-Government | PG&E Attn: Cara Bateman | 707-551-1658 | 1220 Andersen Drive | San Rafael | CA | 94901 | United States | Yes | No | No | No | No | No | No | No | No | No |  |  | Cara Bateman | Senior Environmental Specialist | 707-648-5758 | 2017-03-31 11:07 | 2017-05-23 13:59 | Both Diesel and Unleaded Tanks have been removed. | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031098 |  | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | Pacific Bell W3084 | 2000 Bayhills Dr | San Rafael | 94903 | 38.001 | -122.5049 | Permanent Facility Closure | Other | 44031914 | Facility Owner | 0 | No |  | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 2600 Camino Ramon - Room 3E000 | San Ramon | CA | 94583 | United States | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 308 S. Akard St. Room 1700 | Dallas | TX | 75202 | United States | Non-Government | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 2600 Camino Ramon - Room 3E000 | San Ramon | CA | 94583 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Steven J Hall | Manager, EH&S | (214) 464-3131 | 2022-11-22 05:45 | 2022-11-29 15:02 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031515 | 21-000-300353 | Circle K Stores Inc. | 90141874 | Circle K Stores, Store #5784 | 981 Francisco Boulevard East | San Rafael | 94901 | 37.9609 | -122.5049 | Confirmed/Updated Information | Motor Vehicle Fueling | 44032073 | Tank Owner | 3 | No |  | Circle K Stores Inc. | 657-262-2358 | P.O. Box 52085, Attn: Environmental | Phoenix | AZ | 85072 | United States | Circle K Stores Inc. | 657-262-2358 | P.O. Box 52085, Attn: Environmental | Phoenix | AZ | 85072 | United States | Non-Government | Circle K Stores Inc. | 657-262-2358 | P.O. Box 52085, Attn: Environmental | Phoenix | AZ | 85072 | United States | No | Yes | No | No | No | No | No | No | No | No |  |  | Robert Velasco | Agent For Circle K | 661-250-9300 | 2024-02-06 10:18 | 2024-03-12 10:15 |  | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031551 | 21-000-601073 | County of Marin: Facilities Planning | 90390964 | Sares Regis Group of Northern California | 1600 Los Gamos | San Rafael | 94903 | 38.019 | -122.5412 | New Permit | Other | 44013875 | Facility Operator | 1 | No |  | County of marin Facilities planning | 4154736358 | 3501 Civic Center drive Room 325 | San Rafael | CA | 94903 | United States | County of Marin Facilities planning | 4154736538 | 3501 Civic Center Drive Room 325 | San Rafael | CA | 94903 | United States | County Agency | Sares Regis Group of Northern California | 4154917641 | 1600 Los Gamos Dr Ste 345 | San Rafael | CA | 94903 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2022-12-14 14:08 | 2022-12-19 15:44 | 12.16.2022 submission accepted in lieu of this UST submission | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031569 | 21-000-300371 | Terra Linda 76 & Pro Car Wash | 90100174 | Terra Linda 76 & Pro Car Wash | 921 Del Presidio Boulevard | San Rafael | 94903 | 38.0069 | -122.5449 | Confirmed/Updated Information | Motor Vehicle Fueling | 44051359 | Tank Owner | 2 | No |  | Parminder Singh Grewal | 415-499-3599 | 921 Del Presidio Boulevard | San Rafael | CA | 94903 | United States | Parminder Singh Grewal | 415-499-3599 | 921 Del Presidio Boulevard | San Rafael | CA | 94903 | United States | Non-Government | Parminder Singh Grewal | 415-499-3599 | 921 Del Presidio Boulevard | San Rafael | CA | 94903 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Parminder Singh Grewal | Owner | 415-499-3599 | 2023-11-09 15:15 | 2023-11-09 15:42 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031590 | 21-000-300378 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 1011 Andersen Drive | San Rafael | 94901 | 37.9559 | -122.5041 | Confirmed/Updated Information | Motor Vehicle Fueling | 44013866 | Facility Owner | 3 | No | Keith Nunn, Facility Superintendent | Golden Gate Transit | 415-257-4519 | 1011 Andersen Drive | San Rafael | CA | 94901 | United States | Golden Gate Transit | 415-257-4519 | 1011 Andersen Drive | San Rafael | CA | 94901 | United States | Local Agency/District | Golden Gate Transit | 415-257-4519 | 1011 Andersen Drive | San Rafael | CA | 94901 | United States | Yes | No | No | No | No | No | No | No | No | No |  |  | Karen Shelar | EH&S Specialist | 415-257-4519 | 2023-05-17 09:43 | 2023-05-17 16:46 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031656 | 21-000-300403 | GAWFCO Enterprises, Inc. | 90365647 | San Rafael Valero | 475 Third Street | San Rafael | 94901 | 37.9706 | -122.5176 | Confirmed/Updated Information | Motor Vehicle Fueling | 044047766 | Tank Owner | 3 | No |  | Gawfco Enterprises, Inc. | 925-979-0560 x3 | 3669 Mount Diablo Blvd. | Lafayette | CA | 94549 | United States | Gawfco Enterprises, Inc. | 925-979-0560 x3 | 3669 Mount Diablo Blvd. | Lafayette | CA | 94549 | United States | Non-Government | Gawfco Enterprises, Inc. | 925-979-0560 x3 | 3669 Mount Diablo Blvd. | Lafayette | CA | 94549 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Mohammed N. Ahmadi | President | (925) 979-0560 | 2023-11-07 12:01 | 2024-02-07 15:35 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031959 | 21-000-300524 | Salkhi Family Holdings Inc. | 90130033 | San Rafael Chevron | 440 Third Street | San Rafael | 94901 | 37.9711 | -122.5184 | Confirmed/Updated Information | Motor Vehicle Fueling | 044039245 | Tank Operator | 3 | No |  | Salkhi Family Trust | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Salkhi Family Holdings Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | Salkhi Family Holdings Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Arash Salkhi | President | 415-710-4004 | 2023-12-29 10:56 | 2024-04-17 18:37 |  | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031965 | 21-000-600001 | Salkhi Family Holdings Inc. | 90130033 | Novato Chevron | 7474 Redwood Boulevard | Novato | 94945 | 38.1109 | -122.5684 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048935 | Tank Operator | 4 | No |  | Salkhi Family Trust | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Salkhi Family Holdings Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | Salkhi Family Holdings Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Arash Salkhi | President | 415-710-4004 | 2023-10-13 10:14 | 2023-11-09 13:55 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10031971 | 21-000-600004 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 00524 | 789 Redwood Highway | Mill Valley | 94941 | 37.8963 | -122.5169 | Confirmed/Updated Information | Motor Vehicle Fueling | 228240256 | Tank Owner | 3 | No |  | BP PRODUCTS NORTH AMERICA, INC | 360-970-2296 | PO BOX 6038 | ARTESIA | CA | 90702 | United States | BP PRODUCTS NORTH AMERICA, INC | 360-970-2296 | PO BOX 6038 | ARTESIA | CA | 90702 | United States | Non-Government | MEHRZAD SHAMSIAN | 415-388-8787 | 789 REDWOOD HIGHWAY | MILL VALLEY | CA | 94941 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | 360-371-1500 | 2023-12-29 09:16 | 2024-01-10 00:06 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032106 | 21-000-600061 | Gas & Shop | 90102316 | San Anselmo Gas & Shop | 750 Sir Francis Drake Boulevard | San Anselmo | 94960 | 37.9774 | -122.5624 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048231 | Tank Operator | 3 | No |  | Andy Saberi | 650-588-3088 | 1045 Airport Blvd. | South San Francisco | CA | 94080 | United States | Andy's BP, Inc. | 650-588-3088 | 1045 Airport Blvd. | South San Francisco | CA | 94080 | United States | Non-Government | Andy's BP, Inc. | 415-453-8955 | 1045 Airport Blvd. | South San Francisco | CA | 94080 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Jack Winner | Environmental Compliance | 650-333-5558 | 2024-02-19 13:02 | 2024-02-21 13:27 | field verified 02.21.2024 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | 37.9025 | -122.5113 | Confirmed/Updated Information | Motor Vehicle Fueling | 44052808 | Tank Owner | 4 | No |  | 105 Tiburon Blvd Mill Valley, LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | 105 Tiburon Blvd Mill Valley, LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | Salkhi Petroleum Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Doug Skilling | owner | (415) 383-3050 | 2023-11-28 08:36 | 2024-01-08 11:07 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032112 | 21-000-600064 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron #98933 | 301 Sir Francis Drake Boulevard | Greenbrae | 94904 | 37.9456 | -122.5208 | Confirmed/Updated Information | Motor Vehicle Fueling | 44031913 | Tank Owner | 2 | No |  | SCHULTZ INVESTMENT CO | 415-461-0200 | 50 BON AIR CTR STE 200 | GREENBRAE | CA | 94904 | United States | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | Non-Government | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | No | No | No | No | Yes | No | No | No | No | No |  |  | CHARLES BITTLE | RETAIL HES | 925-842-9002 | 2024-04-29 10:37 | 2024-05-10 10:18 | not field verified - letter of credit meets requirements of 40 CFR 280.112 as allowed by HSC and CCR. | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032118 | 21-000-600067 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 92071 | 22 Rowland Way | Novato | 94945 | 38.0942 | -122.556 | Confirmed/Updated Information | Motor Vehicle Fueling | 44031913 | Tank Owner | 3 | No |  | ROWLAND PLAZA PROPERTY OWNERS ASSOC | (415) 884-9977 | 3 HAMILTON LANDING STE 200 | NOVATO | CA | 94949 | United States | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | (925) 842-9002 | P.O. BOX 6004 ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | Non-Government | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | (925) 842-9002 | P.O. BOX 6004 ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | No | Yes | No | No | No | No | No | No | No | No |  |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | (925) 842-9002 | 2023-12-22 12:01 | 2024-01-31 13:40 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032121 | 21-000-601314 | AS Convenience & Energy Inc. | 90379039 | Strawberry Chevron Gas | 584 Redwood Highway | Mill Valley | 94941 | 37.8898 | -122.5161 | Confirmed/Updated Information | Motor Vehicle Fueling | 245969440 | Tank Owner | 4 | No |  | 584 Redwood Hwy Mill Valley LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | 584 Redwood Hwy Mill Valley LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | AS Convenience & Energy Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-12-08 12:12 | 2024-01-08 09:46 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032184 | 21-000-601233 | Fara's Auto | 90684112 | Fara's Auto | 98 Sir Francis Drake Boulevard | San Anselmo | 94960 | 37.9725 | -122.5614 | Renewal Permit | Motor Vehicle Fueling | 044035485 | Facility Operator | 2 | No | NICK FARA | Nick Fara | 415-306-2928 | 3 LISA DRIVE | san anselmo | CA | 94960 | United States | Fara's Auto | 415-258-0991 | 98 SIR FRANCIS DRAKE BLVD | SAN ANSELMO | CA | 94960 | United States | Non-Government | Fara's Auto | 415-258-0991 | 98 SIR FRANCIS DRAKE BLVD | SAN ANSELMO | CA | 94960 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2024-05-20 17:29 | 2024-05-21 10:35 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032214 | 21-000-600112 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Woodlands | 1 Kent Avenue | Kentfield | 94904 | 37.9508 | -122.5501 | Confirmed/Updated Information | Motor Vehicle Fueling | 44039183 | Tank Operator | 3 | No |  | PETROLEUM SALES INC | 415-256-1600 | 1475 2ND STREET | SAN RAFAEL | CA | 94901 | United States | PETROLEUM SALES INC | 415-256-1600 | 1475 2ND STREET | SAN RAFAEL | CA | 94901 | United States | Non-Government | DS Petroleum, LLC | 415-256-1600 | 1475 2ND STREET | SAN RAFAEL | CA | 94901 | United States | Yes | No | No | No | No | No | Yes | No | No | No |  |  | VERDAN ABREGANA | PROJECT MANAGER | 415-256-1600 | 2024-01-03 12:33 | 2024-01-11 12:26 | field verified 01.11.2024 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032220 | 21-000-601224 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Miller Avenue | 458 Miller Avenue | Mill Valley | 94941 | 37.8952 | -122.5349 | Confirmed/Updated Information | Motor Vehicle Fueling | 44039820 | Tank Operator | 4 | No |  | Petroleum Sales Inc. | 4152561600 | 1475 Second Street | San Rafael | CA | 94901 | United States | Petroleum Sales Inc. | 4152561600 | 1475 Second Street | San Rafael | CA | 94901 | United States | Non-Government | DS Petroleum, LLC | 4152561600 | 1475 Second Street | San Rafael | CA | 94901 | United States | Yes | No | No | No | No | No | Yes | No | No | No |  |  | Albert Uong | UST Operator | 4153885392 | 2024-01-03 09:45 | 2024-01-10 02:50 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032229 | 21-000-600118 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 801 Golden Gate Place | Novato | 94947 | 38.1138 | -122.5677 | Renewal Permit | Motor Vehicle Fueling | 4401386 | Facility Owner | 2 | No | Kellee Hopper | Golden Gate Bridge Highway and Transportation District | (415)455-2000 | 1011 Andersen Drive | San Rafael | CA | 94901 | United States | Golden Gate Bridge Highway and Transportation District | (415) 455-2000 | 1011 Andersen Drive | San Rafael | CA | 94901 | United States | Local Agency/District | Golden Gate Bridge Highway and Transportation District | (415) 455-2000 | 1011 Andersen Drive | San Rafael | CA | 94901 | United States | Yes | No | Yes | No | No | No | No | No | No | No |  |  | Karen Shelar | EH&S Specialist | (415) 257-4519 | 2023-06-12 17:38 | 2023-11-09 13:56 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032250 | 21-000-601334 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 382136/2224 | 2070 REDWOOD HIGHWAY | LARKSPUR | 94939 | 37.9376 | -122.516 | Confirmed/Updated Information | Motor Vehicle Fueling | 44033413 | Tank Operator | 4 | No |  | VIC SOSSIKIAN | 415-924-1042 | 2070 REDWOOD HWY | LARKSPUR | CA | 94904 | United States | VIC SOSSIKIAN | 415-924-1042 | 2070 REDWOOD HWY | LARKSPUR | CA | 94904 | United States | Non-Government | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | No | No | No | No | Yes | No | No | No | No | No |  |  | VIC SOSSIKIAN | OWNER | 415-929-1042 | 2024-04-29 13:45 | 2024-05-10 10:34 | not field verified - letter of credit meets requirements of 40 CFR 280.112 as allowed by HSC and CCR. | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032280 | 21-000-601335 | Rino Fairfax Service | 90763432 | Rino Fairfax Service | 1942 Sir Francis Drake Boulevard | Fairfax | 94930 | 37.9876 | -122.5893 | Renewal Permit | Motor Vehicle Fueling | 842112045 | Tank Operator | 3 | No |  | Keet Nerhan | (650) 726-4402 | P.O. Box 158 | Half Moon Bay | CA | 94019 | United States | Keet Nerhan | (650) 726-4402 | P.O. Box 158 | Half Moon Bay | CA | 94019 | United States | Non-Government | Miguel A. Vargas | (707) 318-3338 | 1942 Sir Francis Drake Blvd. | Fairfax | CA | 94930 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-09-05 10:32 | 2023-09-05 12:51 | field verified during routine inspection 09.05.2023 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032328 | 21-000-600160 | Chevron Station # 91014 | 90621880 | RAJA CROMWELL, INC. | 1549 South Novato Boulevard | Novato | 94947 | 38.0984 | -122.5705 | Transfer Permit | Motor Vehicle Fueling | 44051696 | Facility Owner | 3 | No |  | Dilek Tulca | 415-892-5393 | 1549 S. Novato Blvd | Novato | Ca |  | United States | Dilek Tulca | 415-892-5393 | 1549 S. Novato Blvd | Novato |  |  | United States | Non-Government | Dilek Tulca | 415-892-5393 | 1549 S. Novato Blvd | Novato | CA |  | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-01-11 12:14 | 2023-01-11 12:58 | field verified during routine inspection 01.11.2023 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032337 | 21-000-601283 | Redwood Oil Company, Inc. | 90370903 | Point Reyes Station | 11401 State Route 1 | Pt. Reyes | 94956 | 38.0691 | -122.8063 | Renewal Permit | Motor Vehicle Fueling | 44031876 | Facility Owner | 3 | No |  | Redwood Oil Company | 707-584-7000 | 50 Professional Center Dr. | Rohnert Park | CA | 94928 | United States | Redwood Oil Company | 707-584-7000 | 50 Professional Center Dr. | Rohnert Park | CA | 94928 | United States | Non-Government | Redwood Oil Company | 707-584-7000 | 50 Professional Center Dr. | Rohnert Park | CA | 94928 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Mark Reano | owner | (707) 794-9180 | 2023-02-07 11:06 | 2023-11-09 13:50 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032343 | 21-000-600167 | Marin Municipal Water District | 90097819 | Marin Municipal Water District - Corporation Yard | 220 Tamal Vista Boulevard | Corte Madera | 94925 | 37.9368 | -122.52 | Renewal Permit | Motor Vehicle Fueling | 44013799 | Facility Operator | 1 | No | Safety and Emergency Response Manager | Marin Municipal Water District | (415) 945-1432 | 220 Nellen Ave | Corte Madera | CA | 94925 | United States | Marin Municipal Water District | (415) 945-1432 | 220 Nellen Ave | Corte Madera | CA | 94925 | United States | Local Agency/District | Marin Municipal Water District | (415) 945-1432 | 220 Nellen Ave | Corte Madera | CA | 94925 | United States | Yes | No | No | No | No | No | Yes | No | No | No |  |  | David Peery | Safety and Risk Manager | (415) 945-1432 | 2024-06-05 14:00 | 2024-06-06 12:41 | Update the FR CFO letter. The Marin County CUPA has reviewed the submitted program element and finds the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data. Questions contact Christie.Coleman@marincounty.gov. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032364 | 21-000-600177 | Marin General Hospital | 90103375 | MarinHealth Medical Center | 250 Bon Air Road | Greenbrae | 94904 | 37.9477 | -122.5374 | Confirmed/Updated Information | Other | 44036786 | Tank Owner | 2 | No |  | Marin Health Care District | 415-464-2090 | 100B Drakes Landing Rd | Greenbrea | Ca | 94904 | United States | MarinHealth Medical Center | 415-925-7000 | 250 Bon Air Rd | Greenbrea | Ca | 94904 | United States | Non-Government | MarinHealth Medical Center | 415-925-7000 | 250 Bon Air Rd | Greenbrea | Ca | 94904 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Darren Nakatani | Cheif Engineer | 415-925-7856 | 2024-03-15 17:18 | 2024-04-19 11:59 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032370 | 21-000-600179 | County of Marin | 90404194 | County of Marin/Civic Center Jail | 13 Peter Behr Drive | San Rafael | 94903 | 37.9988 | -122.5339 | Confirmed/Updated Information | Other | 44013875 | Tank Operator | 1 | No | Todd Pressley | County of Marin | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | County of Marin | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913 | United States | County Agency | Patrick McNerney | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Dean Joyner | Environmental Compliance | 415-473-6576 | 2023-12-21 08:28 | 2024-07-17 13:50 | The CFO letter needs to be updated at the end of August, remove yourself as the Tank Operator on the UST Facility Info page and anywhere else (change to County of Marin), your ICC DO cert expires 8/3 so update the DO form, and remove the UST monitoring site plan dated 8/30/02. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032391 | 21-000-600187 | Tamalpais Community Services District | 90103477 | Tamalpais Community Services District | 305 Bell Lane | Mill Valley | 94941 | 37.8757 | -122.5279 | Confirmed/Updated Information | Other | 44725593 | Tank Owner | 2 | No | Mike Quecke | Tamalpais Community Services District | (415) 388-6393 | 305 Bell Lane | Mill Valley | CA | 94941 | United States | Tamalpais Community Services District | (415) 388-6393 | 305 Bell Lane | Mill Valley | CA | 94941 | United States | Local Agency/District | Tamalpais Community Services District | (415) 388-6393 | 305 Bell Lane | Mill Valley | CA | 94941 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Robert Bunce | Public Works Superintendent | (415) 388-6393 | 2023-11-06 13:43 | 2023-11-06 14:47 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032436 | 21-000-600203 | Boyett Petroleum | 90144817 | Corte Madera Kwik Serv - BW # 110 | 516 Tamalpais Drive | Corte Madera | 94925 | 37.9256 | -122.5228 | Renewal Permit | Motor Vehicle Fueling | 44030356 | Tank Operator | 2 | No |  | City of Corte Madera c/o Keegan & Coppin Company, Inc. | (415) 461-1010 | 101 Larkspur Landing Circle, Suite 112 | Larkspur | CA | 94939-1746 | United States | B & W PETROLEUM | 209-577-6000 | 601 McHENRY AVE. | MODESTO | CA | 95350 | United States | Non-Government | B & W PETROLEUM | 209-577-6000 | 601 McHENRY AVE. | MODESTO | CA | 95350 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | B & W PETROLEUM c/o Monica Farhat | Compliance Coordinator | 209-577-6000 | 2024-03-04 09:24 | 2024-08-01 10:59 | field verified during routine AMC testing certification 07.31.2024 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032448 | 21-000-600207 | City of Novato Police Department | 90103690 | City of Novato Police Department | 909 Machin Avenue | Novato | 94945 | 38.1066 | -122.5695 | Renewal Permit | Motor Vehicle Fueling | 44013922 | Tank Operator | 2 | No | Daniel Judd- Equipment Maintenance Supervisor | City of Novato | (415)899-8900 | 922 Machin Ave | Novato | Ca | 94945 | United States | City of Novato | (415)899-8900 | 922 Machin Ave | Novato | Ca | 94945 | United States | Local Agency/District | Daniel Judd -City of Novato | 415-899-8284 | 922 Machin Ave | Novato | Ca | 94945 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Mike Brunelle | Equipment Supervisor | (415)899-8284 | 2023-12-19 14:43 | 2023-12-19 15:15 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032457 | 21-000-600211 | Marin Municipal Water District | 90097819 | Marin Municipal Water District - Ranger Station | 49 Sky Oaks Rd | Fairfax | 94930 | 37.9681 | -122.6043 | Renewal Permit | Motor Vehicle Fueling | 44013799 | Facility Operator | 1 | No | Mark Hedeen - Special Projects, MMWD Operations Division | Marin Municipal Water District | (415) 945-1432 | 220 Nellen Ave | Corte Madera | CA | 94925 | United States | Marin Municipal Water District | (415) 945-1432 | 220 Nellen Ave | Corte Madera | CA | 94925 | United States | Local Agency/District | Marin Municipal Water District | (415) 945-1432 | 220 Nellen Ave | Corte Madera | CA | 94925 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | David Peery | Safety and Risk Manager | (415) 945-1432 | 2022-04-26 12:31 | 2022-10-21 10:23 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032481 | 21-000-600219 | Kentfield and San Francisco Specialty Hospital, Inc. | 90863794 | Kentfield Rehabilitation/Specialty Hospital | 1125 Sir Francis Drake Boulevard | Kentfield | 94904 | 37.9586 | -122.5517 | Confirmed/Updated Information | Other | 44032062 | Tank Owner | 1 | No |  | Vibra Healthcare LLC | 417-591-5700 | 4550 Lena Drive | Mechanicsburg | PA | 17055 | United States | Kentfield Rehabilitation & Specialty Hospital | 415-456-9680 | 1125 Sir Francis Drake Blvd | Kentfield | CA | 94904 | United States | Non-Government | Kentfield Rehabilitation & Specialty Hospital | 415-456-9680 | 1125 Sir Francis Drake Blvd | Kentfield | CA | 94904 | United States | Yes | No | No | No | No | No | No | No | No | No |  |  | Tito B Galvez | Director of Plant Operations | 415-450--1871 | 2019-02-25 12:20 | 2019-05-30 12:51 | Not field verified | Mary Skramstad | Marin County Dept of Public Works CUPA | CUPA
10032493 | 21-000-600223 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - W3176 | 101 Kleinert Way | Tiburon | 94920 | 37.8829 | -122.4649 | Confirmed/Updated Information | Other | 44031914 | Tank Operator | 1 | No |  | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Non-Government | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sarah Bullock | Authorized Agent to AT&T | (800) 566-9347 | 2024-05-31 07:00 | 2024-08-07 13:31 | field verified 08/02/2024 during routine inspection | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032499 | 21-000-600225 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - W3006 | 7 King Street | Larkspur | 94939 | 37.9337 | -122.5352 | Confirmed/Updated Information | Other | 44031914 | Tank Operator | 1 | No |  | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Non-Government | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sarah Bullock | Authorized Agent to AT&T | 1-800-566-9347 | 2024-05-31 06:55 | 2024-06-05 14:32 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032502 | 21-000-600226 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - W3012 | 300 E Blithedale Ave | Mill Valley | 94941 | 37.9033 | -122.5395 | Confirmed/Updated Information | Other | 44031914 | Tank Operator | 1 | No |  | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Non-Government | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sarah Bullock | Authorized Agent to AT&T | 1-800-566-9347 | 2024-05-31 06:57 | 2024-05-31 08:57 | This submittal is to update FR forms. The Marin County CUPA has reviewed the submitted program element and finds the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data. Questions contact Christie.Coleman@marincounty.gov. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032505 | 21-000-600227 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - WC135 | 350 Alameda Del Prado | Novato | 94949 | 38.0623 | -122.5347 | Confirmed/Updated Information | Other | 44031914 | Tank Operator | 1 | No |  | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | Non-Government | Pacific Bell Telephone Company dba AT&T California | (800) 566-9347 | 311 S. Akard Street, Floor 12 | Dallas | TX | 75202 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sarah Bullock | Authorized Agent to AT&T | (800) 566-9347 | 2024-05-31 07:02 | 2024-06-05 14:38 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032508 | 21-000-600228 | Novato Unified School District | 90103927 | NUSD Transportation Yard | 819 Olive Avenue | Novato | 94945 | 38.1099 | -122.5666 | Confirmed/Updated Information | Motor Vehicle Fueling | 44022243 | Facility Owner | 2 | No | Tony Albini | Novato Unified School District | 415-493-4575 | 1015 Seventh Street | Novato | CA | 94945 | United States | Novato Unified School District | 415-493-4575 | 819 Olive Avenue | Novato | CA | 94945 | United States | Local Agency/District | Novato Unified School District | 415-493-4575 | 819 Olive Avenue | Novato | CA | 94945 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Mark Silva | Director of MOT | 145-493-4575 | 2023-06-06 12:11 | 2023-11-09 13:52 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032514 | 21-000-600231 | Sausalito-Marin City Sanitary District | 90103957 | Sausalito-Marin City Sanitary District - Treatment Plant | 1 East Road | Sausalito | 94965 | 37.8432 | -122.4774 | Permanent Facility Closure | Other | 44013908 | Tank Owner | 0 | No | Jeff Kingston, General Manager | Sausalito-Marin City Sanitary District | (415) 332-0244 | 1 East Road | Sausalito | CA | 94965 | United States | Sausalito-Marin City Sanitary District | (415) 332-0244 | 1 East Road | Sausalito | CA | 94965 | United States | Local Agency/District | Sausalito-Marin City Sanitary District | (415) 332-0244 | 1 East Road | Sausalito | CA | 94965 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Omar Arias | Operations Superinendent | (415) 331-4716 | 2018-11-26 07:25 | 2018-11-26 10:35 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032520 | 21-000-600233 | Sausalito-Marin City Sanitary District | 90103957 | Sausalito-Marin City Sanitary District - Main Street PS | 1 Main Street | Sausalito | 94965 | 37.8489 | -122.48 | Permanent Facility Closure | Other | 44013907 | Tank Owner | 0 | No | Jeff Kingston, General Manager | Sausalito Marin City Sanitary District | (415) 332-0244 | 1 East Road | Sausalito | CA | 94965 | United States | Sausalito Marin City Sanitary District | (415) 332-0244 | 1 East Road | Sausalito | CA | 94965 | United States | Local Agency/District | Sasusalito Marin City Sanitary District | (415) 332-0240 | 1 East Road | Sausalito | CA | 94965 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Jeff Kingston | General Manager | (415) 332-0240 | 2022-12-27 10:39 | 2023-01-17 10:07 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032526 | 21-000-600235 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - Trestle Glen PS | 500 Tiburon Boulevard | Tiburon | 94920 | 37.8953 | -122.4877 | Permanent Facility Closure | Other | 44013926 | Tank Owner | 0 | No | Sewerage Agency of Southern Marin | City of Mill Valley | (415) 388-4033 | 26 Corte Madera Avenue | Mill Valley | CA | 94941 | United States | Sewerage Agency of Southern Marin | (415) 388-4033 | 26 Corte Madera Avenue | Mill Valley | CA | 94941 | United States | Local Agency/District | Sewerage Agency of Southern Marin | (415) 388-4033 | 26 Corte Madera Avenue | Mill Valley | CA | 94941 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Chris Monti | Chief Plant Operator | (415) 388-2402 | 2017-02-27 14:20 | 2018-01-17 09:21 | This submittal removes the UST | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032529 | 21-000-600236 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - Salt Works PS | 241 Tiburon Blvd | Tiburon | 94920 | 37.899 | -122.5028 | Permanent Facility Closure | Other | 44013926 | Facility Operator | 0 | No | Mark Grushayev, Wastewater Treatment Manager | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Local Agency/District | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Yes | No | No | No | No | No | No | No | No | No |  |  | Chris Monti | CPO | 4153882402 | 2020-02-13 14:24 | 2020-02-13 14:39 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032532 | 21-000-600237 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - WWTP | 450 Sycamore Avenue | Mill Valley | 94941 | 37.8964 | -122.528 | Permanent Facility Closure | Other | 44013926 | Facility Operator | 0 | No | Mark Grushayev, Wastewater Treatment Manager | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Local Agency/District | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Chris Monti | Chief Plant Operator | (415) 388-2402 | 2018-11-14 13:19 | 2018-11-15 14:59 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032538 | 21-000-600918 | AU Energy LLC | 90129649 | Enfrente Shell #113 | 401 Enfrente Rd | Novato | 94949 | 38.0682 | -122.5391 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2023-11-03 14:33 | 2023-11-09 13:02 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032541 | 21-000-600240 | Xtra Oil - dba Shell Oil | 90104047 | Xtra Oil Co. - dba Chevron | 340 Miller Avenue | Mill Valley | 94941 | 37.8981 | -122.5382 | Confirmed/Updated Information | Motor Vehicle Fueling | 44002652 | Tank Operator | 3 | No |  | Simas M.V. LLC | 510-865-9503 | 2307 Pacific Ave. | Alameda | CA | 94501 | United States | Xtra Oil Company | 510-865-9503 | 2307 Pacific Ave. | Alameda | CA | 94501 | United States | Non-Government | Xtra Oil Company | 510-865-9503 | 2307 Pacific Ave. | Alameda | CA | 94501 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Keith Simas | Operations Supervisor | 510-865-9503 | 2024-02-22 17:26 | 2024-02-22 18:09 | Submittal to update 87 LLD. On your next submittal under UST misc remove test reports and move the statement of understanding under Owner Statement of Designated UST Operator. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032616 | 21-000-600279 | Buck Institute for Age Research | 90104326 | Buck Institute for Research on Aging | 8001 Redwood Boulevard | Novato | 94945 | 38.123 | -122.5666 | Confirmed/Updated Information | Other | 44048711 | Facility Owner | 1 | No |  | Buck Institute for Research on Aging | 4152092000 | 8001 Redwood Blvd | Novato | CA | 94945 | United States | Buck Institute for Research on Aging | 4152092000 | 8001 Redwood Blvd | Novato | CA | 94945 | United States | Non-Government | Buck Institute for Research on Aging | 4152092000 | 8001 Redwood Blvd | Novato | CA | 94945 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Nicole Nannery | EH&S Manager | 4152092281 | 2023-09-22 10:54 | 2023-09-22 15:37 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032634 | 21-000-600919 | AU Energy LLC | 90129649 | DeLong Avenue Shell #112 | 7300 Redwood Blvd | Novato | 94945 | 38.1058 | -122.5702 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 2 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2023-11-07 16:24 | 2023-11-09 12:48 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032919 | 21-000-600412 | Skywalker Properties (5858/3838 LVR) | 90402109 | Skywalker Properties (5858/3838 LVR) | 5858 Lucas Valley Road | Nicasio | 94946 | 38.0584 | -122.6538 | Renewal Permit | Motor Vehicle Fueling | 44047213 | Facility Owner | 2 | No |  | Skywalker Properties LTD., LLC | (415) 662-1704 | P.O. Box 10877 | San Rafael | CA | 94912 | United States | Skywalker Properties LTD., LLC (5858/3838 LVR) | (415) 662-1733 | P.O. Box 10877 | San Rafael | CA | 94912 | United States | Non-Government | Skywalker Properties LTD., LLC (5858/3838 LVR) | (415) 662-1733 | P.O. Box 10877 | San Rafael | CA | 94912 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Craig Weichel | Senior Fire Captain | (415) 662-1703 | 2024-05-13 09:34 | 2024-05-14 09:24 | Your UST Certification of Financial Responsibility Documentation, please update with the current insurance policy information. This acceptance is only for the UST structural certifications. All other data and documents were not reviewed. Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10033030 | 21-000-600459 | Corte Madera Town Center | 90105889 | Town Center Corte Madera | 100 Corte Madera Town Center | Corte Madera | 94925 | 37.9297 | -122.5168 | Confirmed/Updated Information | Other | 44045966 | Facility Owner | 0 | No |  | 770 Tamalpais Drive, Inc. | (415) 924-2961 | 100 Corte Madera Town Center | Corte Madera | CA | 94925 | United States | 770 Tamalpais Drive, Inc. | (415) 924-2961 | 100 Corte Madera Town Center | Corte Madera | CA | 94925 | United States | Non-Government | Town Center Corte Madera | (415) 924-2961 | 100 Corte Madera Town Center | Corte Madera | CA | 94925 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Thomas Guilfoyle | Director of Facilities | (415) 924-2961 | 2016-11-07 14:07 | 2016-11-07 14:27 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10033207 | 21-000-601284 | CB Aviation, Inc DBA CB SkyShare | 90713596 | CB Aviation Inc. DBA, CB Sky Share | 351 Airport Road | Novato | 94945 | 38.1403 | -122.5575 | Renewal Permit | Other | 44037613 | Tank Owner | 2 | No |  | County of Marin | 415-897-1754 | 3501 Civic Center Dr. | San Rafael | CA | 94903 | United States | CB Aviation Inc. DBA, CB Sky Share | 415-897-1653 | 351 Airport Drive | Novato | CA | 94945 | United States | Non-Government | CB Aviation Inc. DBA, CB Sky Share | 415-897-1653 | 351 Airport Drive | Novato | CA | 94945 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | TJ Neff | Managing Partner | 415-897-1653 | 2023-06-05 12:16 | 2023-09-21 13:26 | Field inspection conducted 09.12.2023. | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10033372 | 21-000-600625 | County of Marin | 90404194 | County of Marin/Civic Center-Bldg Eng Tank | 3501 Civic Center Drive | San Rafael | 94903 | 37.9975 | -122.5292 | Confirmed/Updated Information | Other | 44013875 | Tank Operator | 1 | No | Todd Pressley | County of Marin | 415-473-6576 | P.O. Box 4186 | San Rafael | CA | 94913 | United States | County of Marin | 415-473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | County Agency | Patrick McNerney | 415-473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Dean Joyner | Environmental Compliance | 415-473-6576 | 2023-12-21 15:27 | 2024-07-17 13:51 | The CFO letter needs to be updated at the end of August so youll need to update the CFO letter for all 3 UST sites. Your ICC DO cert expires 8/3/2024 so youll need to update the DO form for all 3 UST sites. I recommend removing yourself as the Tank Operator on the UST Facility Info page and anywhere else (change to County of Marin). | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10141619 | 21-000-601189 | Frontier California, Inc. | 90000160 | Frontier California, Inc.: Novato CO | 911 Diablo Avenue | Novato | 94947 | 38.1039 | -122.5731 | Confirmed/Updated Information | Other | 44007526 | Tank Owner | 1 | No |  | Frontier California Inc. | 909-620-5962 | 280 S. Locust Street | Pomona | CA | 91766 | United States | Frontier California Inc. | 909-620-5962 | 280 S. Locust Street | Pomona | CA | 91766 | United States | Non-Government | Frontier California Inc. | 909-620-5962 | 280 S. Locust Street | Pomona | CA | 91766 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Masood Choudhury | Global EH&S Manager | 909-620-5962 | 2023-09-13 13:30 | 2023-11-09 12:57 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10156219 | 21-000-300238 | United Parcel Service, Inc. | 90129202 | UPS - San Rafael | 2985 Kerner Blvd | San Rafael | 94901 | 37.955 | -122.4981 | Renewal Permit | Motor Vehicle Fueling | 44032294 | Tank Operator | 1 | No |  | United Parcel Service, Inc. | 3232299894 | 55 Glenlake Parkway, NE | Atlanta | CA | 30328 | United States | United Parcel Service, Inc. | 3232299894 | 8400 Pardee Drive | Oakland | CA | 94621 | United States | Non-Government | United Parcel Service, Inc. | 3232299894 | 8400 Pardee Drive | Oakland | CA | 94621 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Carlos Medina | District Plant Engineering Manager | 510-453-2090 | 2023-07-17 13:41 | 2023-08-29 09:25 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10156585 | 21-000-600825 | Safeway, Inc. | 90129313 | Safeway Fuel Center #2828 | 5700 Nave Drive | Novato | 94949 | 38.062 | -122.5326 | Confirmed/Updated Information | Motor Vehicle Fueling | 044040801 | Tank Owner | 4 | No |  | Madison Marquette Retail Services | 415-277-6839 | 909 Montgomery St, Suite 200 | San Francisco | CA | 94133 | United States | Safeway, Inc. | 925-469-7000 | 5918 Stoneridge Mall Rd. | Pleasanton | CA | 94588 | United States | Non-Government | Safeway, Inc. | 925-467-3000 | PO Box 9070 / 6000 Stoneridge Mall Rd. | Pleasanton | CA | 94588 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Ron Lee | Environmental Manager | 925-469-7513 | 2023-12-29 11:14 | 2024-01-31 13:16 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342432 | 21-000-600275 | County of Marin | 90404194 | County of Marin/Civic Center Garage | 6 Peter Behr Drive | San Rafael | 94903 |  |  | Confirmed/Updated Information | Other | 44013875 | Tank Operator | 2 | No | Todd Pressley | County of Marin | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | County of Marin | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | County Agency | Patrick McNerney | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Dean Joyner | Environmental Compliance | 415-499-6576 | 2024-01-04 08:26 | 2024-07-17 13:50 | The CFO letter needs to be updated at the end of August, remove yourself as the Tank Operator on the UST Facility Info page and anywhere else (change to County of Marin), and your ICC DO cert expires 8/3 so update the DO form. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342462 | 21-000-600645 | Matt and Jeff's Car Wash | 90308275 | Matt and Jeff's Car Wash | 125 Vintage Way | Novato | 94945 | 38.0915 | -122.5569 | Confirmed/Updated Information | Motor Vehicle Fueling | 44042448 | Facility Owner | 3 | No |  | Vintage Way Car Wash, Inc. | 415-899-9952 | 125 Vintage Way | Novato | CA | 94945 | United States | Vintage Way Car Wash, Inc. | 415-899-9952 | 125 Vintage Way | Novato | CA | 94945 | United States | Non-Government | Vintage Way Car Wash, Inc. | 415-899-9952 | 125 Vintage Way | Novato | CA | 94945 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Matt Broderick | Treasurer/Secretary | 415-899-9952 | 2022-08-23 12:46 | 2023-08-10 12:42 | field verified 08.07.2023 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342474 | 21-000-600653 | Bridgeway Gas | 90308284 | Bridgeway Gas | 1103 Bridgeway | Sausalito | 94965 | 37.8587 | -122.4843 | Renewal Permit | Motor Vehicle Fueling | 44013944 | Facility Owner | 3 | No |  | David & Sandra Mann | (415) 332-4007 | 1103 Bridgeway | Sausalito | CA | 94965 | United States | David & Sandra Mann | (415) 332-4007 | 1103 Bridgeway | Sausalito | CA | 94965 | United States | Non-Government | David & Sandra Mann | (415) 332-4007 | 1103 Bridgeway | Sausalito | CA | 94965 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Sandra Mann | facility owner | (415) 331-1235 | 2024-01-17 13:23 | 2024-01-17 14:44 | Not field verified.Next reporting due date listed based on date CFO letter lapses. | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342489 | 21-000-600664 | Bolinas Gas Station | 90308299 | Bolinas Gas Station | 6 Wharf Road | Bolinas | 94924 | 37.9094 | -122.686 | Confirmed/Updated Information | Motor Vehicle Fueling | 44043195 | Facility Owner | 3 | No |  | Bolinas Community Land Trust, Inc. | (415) 868-8880 | P.O. Box 805 | Bolinas | CA | 94924 | United States | Bolinas Community Land Trust, Inc. | (415) 868-8880 | P.O. Box 805 | Bolinas | CA | 94924 | United States | Non-Government | Bolinas Community Land Trust, Inc. | (415) 868-8880 | P.O. Box 805 | Bolinas | CA | 94924 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Albert Foreman | Manager | (415) 509-1997 | 2023-11-10 10:58 | 2023-11-19 21:54 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342510 | 21-000-600721 | Salkhi Family Holdings Inc. | 90130033 | 570 Redwood Valero | 570 Redwood Highway | Mill Valley | 94941 | 37.8887 | -122.5158 | Confirmed/Updated Information | Motor Vehicle Fueling | 44039836 | Tank Owner | 3 | No |  | Salkhi Family Trust | 415-710-4004 | 10 Bay Way | San Rafael | CA | 94901 | United States | Salkhi Family Trust | 415-710-4004 | 10 Bay Way | San Rafael | CA | 94901 | United States | Local Agency/District | Salkhi Family Holdings Inc | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-12-08 13:01 | 2024-01-08 12:03 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342513 | 21-000-600722 | Salkhi Family Holdings Inc. | 90130033 | Mill Valley Chevron | 5 Ashford Avenue | Mill Valley | 94941 | 37.9039 | -122.5229 | Confirmed/Updated Information | Motor Vehicle Fueling | 44044598 | Tank Operator | 3 | No |  | Ali Salkhi | (415) 710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Salkhi Family Holdings Inc. | (415) 710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | Salkhi Family Holdings Inc. | (415) 710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Arash Salkhi | President | (415) 710-4004 | 2023-12-08 12:46 | 2024-01-08 11:59 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342591 | 21-000-601313 | AS Convenience & Energy Inc. | 90379039 | STRAWBERRY CHEVRON FOOD MART | 580 Redwood Highway | Mill Valley | 94941 | 37.8894 | -122.5159 | Confirmed/Updated Information | Motor Vehicle Fueling | 203960864 | Tank Owner | 4 | No |  | 580 Redwood Hwy Mill Valley LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | 580 Redwood Hwy Mill Valley LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | AS Convenience & Energy Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-12-08 12:17 | 2024-01-08 08:58 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342663 | 21-000-601292 | GAWFCO Enterprises, Inc. | 90365647 | RedHill Convenience & Fuel | 930 Sir Francis Drake Boulevard | San Anselmo | 94960 | 37.9812 | -122.5666 | Confirmed/Updated Information | Motor Vehicle Fueling | 044047766 | Tank Owner | 2 | No |  | GAWFCO Enterprises, Inc. | 925-979-0560 | 3669 Mount Diablo Blvd. | Lafayette | CA | 94549 | United States | GAWFCO Enterprises, Inc. | 925-979-0560 | 3669 Mount Diablo Blvd. | Lafayette | CA | 94549 | United States | Non-Government | GAWFCO Enterprises, Inc. | 925-979-0560 | 3669 Mount Diablo Blvd. | Lafayette | CA | 94549 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2023-11-07 10:31 | 2024-03-19 12:00 | field verified 03.19.2024 during routine inspection | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342681 | 21-000-600823 | HQ Fuels | 90308479 | HQ Fuels | 251 Shoreline Highway | Mill Valley | 94941 | 37.8818 | -122.5253 | Confirmed/Updated Information | Motor Vehicle Fueling | 44046379 | Facility Owner | 4 | No |  | Marin Properties, LLC | (650) 464-2360 | 459 Neptune Drive | Redwood City | CA | 94065 | United States | HQ Fuels | (650) 464-2360 | 251 Shoreline Highway | Mill Valley | CA | 94941 | United States | Non-Government | HQ Fuels | (650) 464-2360 | 251 Shoreline Highway | Mill Valley | CA | 94941 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Louis Saadeh | owner | (650) 464-2360 | 2024-02-11 21:35 | 2024-02-12 07:48 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342696 | 21-000-600838 | Power Petroleum Corporation | 90308494 | Power Petroleum Corporation | 1320 Second Street | San Rafael | 94901 | 37.9717 | -122.5319 | Confirmed/Updated Information | Motor Vehicle Fueling | 44041768 | Facility Operator | 4 | No |  | Sunrise San Rafael LLC | 1-310-694-5062 | 11601 Wilshire Blvd. Suite 1680 | Los Angeles | CA | 90025 | United States | Sunrise San Rafael LLC | 1-310-694-5062 | 11601 Wilshire Blvd Suite 1680 | Los Angeles | CA | 90025 | United States | Non-Government | Power Petroleum Corporation | 1-415-810-7136 | 5153 Diamond Heights Blvd. | San Francisco | CA | 94131 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Robert Poquez | Owner/Operator | 415-482-8135 | 2023-12-22 11:20 | 2023-12-22 11:42 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342789 | 21-000-600888 | Northgate Gas | 90308581 | Northgate Gas | 77 San Pablo Avenue | San Rafael | 94903 | 37.9963 | -122.5284 | Confirmed/Updated Information | Motor Vehicle Fueling | 44224389 | Tank Operator | 3 | No |  | Haji Alan | (510) 862-3333 | 77 San Pablo Ave. | San Rafael | CA | 94903 | United States | Haji Alan | (510) 862-3333 | 77 San Pablo Ave. | San Rafael | CA | 94903 | United States | Non-Government | Shahram Shahnazi | (415) 419-1477 | 77 San Pablo Ave. | San Rafael | CA | 94903 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Shahram Shahznazi | Business Owner | 415-272-3824 | 2023-12-28 12:00 | 2023-12-28 12:17 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342822 | 21-000-601067 | A&A GAS INC | 90308611 | Marin Gas & Auto Service | 600 Magnolia Avenue | Larkspur | 94939 | 37.938 | -122.5342 | Confirmed/Updated Information | Motor Vehicle Fueling | 44049703 | Facility Operator | 4 | No |  | MO MASHOON | 5108919988 | 428 13TH ST 10TH FLOOR 13TH AT BROADWAY | OAKLAND | CA | 94612 | United States | GHULAM ALI | 4159241616 | 600 MAGNOLIA AVE | LARKSPUR | CA | 94939 | United States | Non-Government | GHULAM ALI | 4159241616 | 600 MAGNOLIA AVE | LARKSPUR | CA | 94939 | United States | No | No | No | No | No | No | No | Yes | No | No |  |  | GHULAM ALI | PRESIDENT | 4159241616 | 2023-11-08 16:16 | 2023-11-08 16:26 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342855 | 21-000-600916 | AU Energy LLC | 90129649 | Miwok Shell #109 | 7473 Redwood Blvd | Novato | 94945 | 38.1111 | -122.5695 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2023-11-03 14:54 | 2023-12-21 13:38 | Field verified during routine inspection 12.21.2023. | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342858 | 21-000-600917 | AU Energy LLC | 90129649 | Novato Shell #110 | 1390 S. Novato Blvd | Novato | 94947 | 38.0879 | -122.5645 | Confirmed/Updated Information | Motor Vehicle Fueling | 044048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2023-11-03 16:27 | 2023-11-09 13:59 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342870 | 21-000-600920 | AU Energy LLC | 90129649 | West Novato Shell #111 | 2085 Novato Boulevard | Novato | 94947 | 38.1118 | -122.5936 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae Street | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae Street | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae Street | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2023-11-03 16:32 | 2023-11-09 12:51 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342876 | 21-000-600922 | AU Energy LLC | 90129649 | Northgate Shell #118 | 950 Del Presidio Boulevard | San Rafael | 94901 | 38.0069 | -122.5439 | Confirmed/Updated Information | Motor Vehicle Fueling | 044048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2024-06-18 14:32 | 2024-07-05 14:45 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342879 | 21-000-600923 | AU Energy LLC | 90129649 | Drake Shell #106 | 295 Sir Francis Drake Boulevard | Greenbrae | 94904 | 37.9453 | -122.5204 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 3 | No |  | AU Energy, LLC | (510) 657-9150 | 41805 Albrae Street | Fremont | CA | 94538 | United States | AU Energy, LLC | (510) 657-9150 | 41805 Albrae Street | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | (510) 657-9150 | 41805 Albrae Street | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | (510) 657-9150 | 2024-07-17 16:54 | 2024-07-22 13:14 | field verified 07.17.2024 during routine AMC | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | 37.9708 | -122.521 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2024-07-03 11:45 | 2024-07-24 14:00 | UST tank monitoring systems field verified 07.23.2024 during permitted cold start monitoring testing. | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | 37.9739 | -122.5403 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048001 | Tank Owner | 3 | No |  | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | Non-Government | AU Energy, LLC | 510-657-9150 | 41805 Albrae St | Fremont | CA | 94538 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Sunny Goyal | Project Manager | 510-657-9150 | 2024-06-18 13:58 | 2024-06-24 15:09 |  | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10342927 | 21-000-601153 | Apro LLC | 90161914 | United #5651 | 250 Tiburon Boulevard | Tiburon | 94920 | 37.8983 | -122.5009 | Confirmed/Updated Information | Motor Vehicle Fueling | 044040092 | Facility Operator | 2 | No |  | Convenience Retailers LLC | 925-884-0800 | 7180 Koll Center Pkwy | Pleasanton | Ca | 94566 | United States | APRO LLC | 310-323-3992 | 4130 Cover Street | Long Beach | Ca | 90808 | United States | Non-Government | APRO LLC | 310-323-3992 | 4130 Cover Street | Long Beach | Ca | 90808 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Allen Faass | Compliance | 925-884-0800 | 2024-01-18 12:26 | 2024-01-22 01:31 | Maintain current insurance cert onsite and available during the annual UST inspection. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342954 | 21-000-600954 | Sausalito Shell | 90308737 | ANABI OIL CORP DBA SAUSALITO SHELL | 2901 Bridgeway | Sausalito | 94965 | 37.8691 | -122.5035 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048118 | Tank Owner | 3 | No |  | Anabi Real Estate Dev., LLC | (909) 394-4728 | 1450 N Benson Avenue Suite A | Upland | CA | 91786 | United States | Anabi Real Estate Dev., LLC | (909) 394-4728 | 1450 N Benson Avenue Suite A | Upland | CA | 91786 | United States | Non-Government | DECW-Sausalito, LLC | 707-266-8524 | 2901 Bridgeway Blvd. | Sausalito | CA | 94965 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Summer Ireifej | Controller | (909) 394-4728 | 2024-05-06 15:01 | 2024-05-07 15:21 | Violation corrected on tanks #1 and 2 and the o/o agreement | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342957 | 21-000-601424 | RADC Enterprises Inc. | 90366556 | Novato Shell | 5821 Nave Drive | Novato | 94949 | 38.064 | -122.5346 | Confirmed/Updated Information | Motor Vehicle Fueling | 044048118 | Tank Owner | 3 | No |  | Anabi Real Estate Dev., LLC | 909-394-4728 | 1450 N Benson Avenue Suite A | Upland | CA | 91786 | United States | Anabi Real Estate Dev., LLC | 909-394-4728 | 1450 N Benson Avenue Suite A | Upland | CA | 91786 | United States | Non-Government | RADC Enterprises, Inc. | 909-394-4728 | 1450 N Benson Avenue Suite A | Upland | CA | 91786 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Summer Ireifej | Controller | 909-394-4728 | 2023-11-06 16:44 | 2023-11-09 12:52 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342990 | 21-000-600969 | North Bay Gas | 90308770 | North Bay Gas | 1789 Sir Francis Drake Boulevard | Fairfax | 94930 | 37.987 | -122.5865 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048317 | Tank Owner | 3 | No |  | Dusty Divine | 415-457-0220 | 1789 Sir Francis Drake Boulevard | Fairfax | CA | 94930 | United States | Shahram Shahmaz | 415-272-3824 | 74 Glen Drive | Sausalito | CA | 94965 | United States | Non-Government | Shahram Shahmaz | 415-272-3824 | 74 Glen Drive | Sausalito | CA | 94965 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Shahram Shahmaz | Owner | 415-272-3824 | 2023-12-28 12:18 | 2023-12-28 12:26 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342996 | 21-000-601202 | BRENTWOOD GAS & MORE | 90615466 | Corte Madera Gas | 700 Tamalpais Drive | Corte Madera | 94925 | 37.9253 | -122.5185 | Confirmed/Updated Information | Motor Vehicle Fueling | 219954720 | Tank Owner | 2 | No |  | Sodhi Group USA | 925-301-7783 | 700 Tamalpais Dr | Corte Madera | CA | 94925 | United States | Sukhwinder Singh | 925-301-7783 | 700 Tamalpais Dr | Corte Madera | CA | 94925 | United States | Non-Government | Sukhwinder Singh | 925-301-7783 | 700 Tamalpais Dr | Corte Madera | CA | 94925 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2024-01-04 07:19 | 2024-01-10 03:04 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342999 | 21-000-601571 | Elite Gas & Mart 1 | 90860245 | Mobil | 34 Ritter Street | San Rafael | 94901 | 37.9709 | -122.5245 | Confirmed/Updated Information | Motor Vehicle Fueling | 44053116 | Facility Operator | 3 | No |  | TD PROPERTY HOLDINGS INC. | 510-759-2384 | 34 Ritter Street | San Rafael | CA | 94901 | United States | Elite Gas & Mart 1 | 408-340-0236 | 785 Ellerbrook St | Mountain House |  | 95391 | United States | Non-Government | Elite Gas & Mart 1 | 408-340-0236 | 785 Ellerbrook St | Mountain House |  | 95391 | United States | No | No | Yes | No | No | No | Yes | No | No | No |  |  | LISA THOMPSON | COMPLIANCE MANAGER | (818) 336-8984 | 2024-05-15 12:51 | 2024-05-15 13:17 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10343002 | 21-000-600974 | Sillada Union 76 #257384 | 90308782 | Sillada Union 76 #257384 | 1125 Lincoln Ave | San Rafael | 94901 | 37.9742 | -122.5238 | Confirmed/Updated Information | Motor Vehicle Fueling | 44048959 | Facility Owner | 2 | No |  | Estate of Sa-Ngasilpa Pungprakearti | (707) 332-8562 | 1125 Lincoln Ave | San Rafael | CA | 94901 | United States | Estate of Sa-Ngasilpa Pungprakearti | (707) 332-8562 | 1125 Lincoln Ave | San Rafael | CA | 94901 | United States | Non-Government | Estate of Sa-Ngasilpa Pungprakearti | (707) 332-8562 | 1125 Lincoln Ave | San Rafael | CA | 94901 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Sa-Ngasilpa Pungprakearti | Owner | (415) 456-5452 | 2023-01-20 16:05 | 2023-03-28 15:37 |  | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10343047 | 21-000-601567 | AS Convenience & Energy Inc. | 90379039 | Terra Linda Gas | 1005 Northgate Drive | San Rafael | 94903 | 38.0085 | -122.5451 | Confirmed/Updated Information | Motor Vehicle Fueling | 44111111 | Tank Owner | 2 | No |  | 2100 Springs Road Vallejo, LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | AS Convenience & Energy Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | AS Convenience & Energy Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | ROBERT ANDREW LEUZINGER | PRESIDENT/CFO | (707) 494-5215 | 2024-04-25 15:40 | 2024-05-09 11:03 | not field verified | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10343053 | 21-000-600996 | Mill Valley Gas & Mart | 90694231 | Mill Valley Gas & Mart | 630 Blithedale Avenue East | Mill Valley | 94941 | 37.9001 | -122.5285 | Permanent Facility Closure | Motor Vehicle Fueling | 44043255 | Tank Owner | 0 | No |  | Mash Petroleum | (510) 891-9988 | 428 13th Street, 10th Floor | Oakland | CA | 94941 | United States | Mash Petroleum | (510) 891-9988 | 428 13th Street, 10th Floor | Oakland | CA | 94941 | United States | Non-Government | Mash Petroleum | (510) 891-9988 | 428 13th Street, 10th Floor | Oakland | CA | 94941 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2017-06-26 10:23 | 2017-06-26 10:35 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343068 | 21-000-601069 | Salkhi | 90388270 | Fairfax Gas | 2001 Sir Francis Drake Boulevard | Fairfax | 94930 | 37.9874 | -122.5902 | Permanent Facility Closure | Motor Vehicle Fueling | 4404982 | Facility Owner | 0 | No |  | Salkhi Petroleum, Inc. | 415-710-4004 | 7474 Redwood Blvd. | Novato | CA | 94945 | United States | Salkhi Petroleum, Inc. | 415-710-4004 | 7474 Redwood Blvd. | Novato | CA | 94945 | United States | Non-Government | Salkhi Petroleum, Inc. | 415-710-4004 | 7474 Redwood Blvd. | Novato | CA | 94945 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Arash Salkhi | President | 415-710-4004 | 2017-06-05 16:25 | 2017-06-12 08:08 |  | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10343089 | 21-000-601158 | Apro LLC | 90161914 | United # 5662 | 100 Marinwood Avenue | San Rafael | 94903 | 38.0331 | -122.5404 | Confirmed/Updated Information | Motor Vehicle Fueling | 044040092 | Tank Owner | 4 | No |  | Marinwood Plaza LLC | 925-884-0800 | 1710 Novato Blvd. | Novato | Ca | 94947 | United States | APRO LLC | 925-884-0800 | 4130 Cover Street | Long Beach | Ca | 90808 | United States | Non-Government | APRO LLC | 310-323-3992 | 4130 Cover Street | Long Beach | Ca | 90808 | United States | No | No | Yes | No | No | No | No | No | No | No |  |  | Allen Faass | Compliance | 925-884-0800 | 2024-01-18 12:39 | 2024-04-09 17:01 | Accepted but check your BOE number - there isn't a 0 in the front. And remove the miscellaneous doc uploaded. These have been saved by Marin CUPA and don't need to be uploaded with every submittal. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10460464 | 21-000-600116 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 94737/1570 | 90 Madera Blvd | Corte Madera | 94925 | 37.9294 | -122.5162 | Confirmed/Updated Information | Motor Vehicle Fueling | 44031913 | Tank Owner | 3 | No |  | 770 TAMALPAIS DRIVE INC | 415-924-7062 | 100 CORTE MADERA TWN CTR | CORTE MADERA | CA | 94925 | United States | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | Non-Government | CHEVRON PRODUCTS COMPANY (A DIVISION OF CHEVRON U.S.A. INC.) | 925-842-9002 | P.O. BOX 6004, ATTN: PERMIT DESK | SAN RAMON | CA | 94583 | United States | No | No | No | No | Yes | No | No | No | No | No |  |  | CHARLES BITTLE | RETAIL HES | 925-842-9002 | 2024-04-29 14:39 | 2024-05-13 19:05 | FR and DO forms updated. | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10473877 | 21-000-600098 | CDCR - California State Prison | 90102631 | CDCR - California State Prison San Quentin | 1 Main St | San Quentin | 94964 | 37.9417 | -122.4829 | Confirmed/Updated Information | Other | 44032062 | Facility Owner | 3 | No | CHANCE ANDES, WARDEN | STATE OF CALIF - CDCR-SAN QUENTIN | 415-455-5000 | 1 MAIN ST | SAN QUENTIN | CA | 94964 | United States | STATE OF CALIF - CDCR-SAN QUENTIN | 415-455-5000 | 1 MAIN ST | SAN QUENTIN | CA | 94964 | United States | State Agency | CDCR - SAN QUENTIN REHABILITATION CENTER | 415-455-5000 | 1 MAIN ST | SAN QUENTIN | CA | 94964 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | RON DAVIS | WARDEN | 415-455-5000 | 2024-03-28 13:36 | 2024-06-10 13:48 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10483969 | 21-000-600060 | Novato 76 | 90410779 | Novato 76 | 375 Ignacio Blvd | Novato | 94949 | 38.0657 | -122.5402 | Confirmed/Updated Information | Motor Vehicle Fueling | 44046460 | Tank Owner | 3 | No |  | ARMSCO, Inc. | 415-531-1131 | P.O. Box 5427 | Novato | CA | 94948 | United States | ARMSCO, Inc. | 415-531-1131 | P.O. Box 5427 | Novato | CA | 94948 | United States | Non-Government | ARMSCO, Inc. | 415-531-1131 | P.O. Box 5427 | Novato | CA | 94948 | United States | No | No | No | No | No | No | Yes | No | No | No |  |  | Ali M. Mahmoodi | Owner | 415-531-1131 | 2023-01-11 13:28 | 2023-04-10 12:57 | The Marin County CUPA has reviewed the submitted program element and finds that the data and/or document(s) meet state and local reporting requirements. The CUPA has not necessarily field-verified the submitted data.Sincerely,Michael Farynamfaryna@marincounty.org+1 (415) 473-2027 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10500199 | 21-000-600234 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - Ricardo Rd PS | 10 Seminary Dr | Mill Valley | 94941 | 37.891 | -122.5156 | Permanent Facility Closure | Other | 44013926 | Facility Operator | 0 | No | Mark Grushayev, Wastewater Treatment Manager | City of Mill Valley | (415) 388-4033 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | Local Agency/District | Sewerage Agency of Southern Marin | (415) 388-2402 | 26 Corte Madera Ave. | Mill Valley | CA | 94941 | United States | No | No | Yes | No | No | No | Yes | No | No | No |  |  | Chris Monti | CPO | 4153882402 | 2019-11-22 12:32 | 2019-11-22 13:29 |  | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10810900 | 21-000-601315 | AS Convenience & Energy Inc. | 90379039 | 24/7 Kentfield | 2066 Redwood Hwy | Greenbrae | 94939 | 37.9386 | -122.5154 | Confirmed/Updated Information | Motor Vehicle Fueling | 244388384 | Tank Owner | 3 | No |  | 2066 Redwood Hwy Greenbrae LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | 2066 Redwood Hwy Greenbrae LLC | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | Non-Government | AS Convenience & Energy Inc. | 415-710-4004 | PO BOX 1678 | San Leandro | CA | 94577 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2024-07-11 10:10 | 2024-07-11 14:22 | field verified during routine inspection 06.25.2024 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10957150 |  | County of Marin | 90404194 | County of Marin/BB2 Site | 636 Sir Francis Drake Blvd | San Anselmo | 94960 | 37.977 | -122.562 | New Permit | Other | 440000000 | Tank Owner | 1 | No | Tracy Clay | County of Marin | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | County of Marin | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | County Agency | Patrick McNerney | (415) 473-6576 | P.O. Box 4186 | San Rafael | CA | 94913-4186 | United States | No | No | No | No | No | No | Yes | No | No | No | [5 empty] | 2024-06-06 15:56 | 2024-06-11 08:42 | Marin CUPA will issue invoice for closure activities, should you have any questions please contact Julia Barnes at 415-473-7085 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA

## UST Tank & Monitoring Plan Info
Facility Identification and Location | [7 empty] | General UST Tank Permit Info | [10 empty] | Tank Use and Contents |  |  |  |  | Tank Construction |  |  |  |  | Tank Overfill Prevention |  |  |  | Product / Waste Piping Construction | [6 empty] | Vent Piping Construction |  |  |  | Vent Piping Transition Sumps | Vapor Recovery (VR) Piping Construction |  |  |  | Riser / Fill Pipe Piping Construction |  |  |  | Fill Components Installed |  |  | Under Dispenser Containment (UDC) |  |  | Corrosion Prevention |  |  | UST Tank Certification / Applicant Information |  |  | Equipment Testing and Preventive Maintenance |  | Site Plot Plan Submitted | Continuous Electronic Tank Monitoring | [5 empty] | Automatic Tank Gauging | [8 empty] | Monthly Statistical Inventory Reconciliation | Weekly Manual Tank Gauge |  | Tank Integrity Testing |  |  | Other Tank Monitoring |  | Continuous Monitoring of Piping Secondary Containment | [7 empty] | Mechanical Line Leak Detector Performs 3 GPH Leak Test |  |  | Electronic Line Leak Detector Performs 3 GPH Leak Test | [5 empty] | Pipeline Integrity Testing |  |  | Visual Pipeline Monitoring |  | Suction Piping Meets Exemption Criteria | No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System | Other Pipeline Monitoring |  | Under Dispenser Containment (UDC) Monitoring | [12 empty] | Periodic System Testing |  |  | Recordkeeping | [7 empty] | Training | [9 empty] | Comments and Additional Information | Personnel Responsibilities |  |  |  | UST Monitoring Plan Certification / Applicant Information |  |  |  | Submittal / Acceptance Information |  |  | Regulator Information
1a | 1 |  |  | 3 | 103 | 104 |  | 430 | 432 | 432-a | 433 | 434 | 436 | 435 | 430-a | 430-b | 437 | 438 | 439 | 439a | 440 | 440a | 440b | 443 | 444 | 444a | 445 | 445a | 452a | 452b | 452c | 452d | 460 | 458 | 464 | 464a | 464b | 464c | 464d | 464e | 464e1 | 464f | 464f1 | 464i | 464g | 464g1 | 464h | 464h1 | 464j | 464j1 | 464k | 464k1 | 451-a | 451-b | 451-c | 469a | 469b | 469c | 448a | 448b | 448c | 470 | 471 | 472 | 490-3a | 490-3b | 490-4 | 490-5 | 490-6 | 490-7 | 490-8 | 490-9 | 490-10 | 490-11 | 490-12 | 490-13 | 490-14 | 490-15 | 490-16 | 490-17 | 490-18 | 490-19 | 490-20 | 490-21 | 490-22 | 490-23 | 490-24 | 490-25 | 490-26 | 490-27 | 490-28 | 490-29 | 490-30 | 490-31 | 490-32 | 490-33 | 490-34 | 490-35 | 490-36 | 490-37 | 490-38 | 490-39 | 490-40 | 490-41 | 490-42 | 490-43 | 490-44 | 490-45 | 490-46 | 490-47 | 490-48 | 490-49 | 490-50 | 490-51 | 490-52 | 490-53 | 490-54a | 490-54b | 490-55 | 490-56 | 490-57 | 490-58 | 490-59 | 490-60 | 490-61 | 490-62 | 490-63 | 490-64a | 490-64b | 490-65 | 490-66 | 490-67 | 490-68a | 490-68b | 490-68c | 490-68d | 490-68e | 490-68f | 490-68g | 490-68h | 490-69a | 490-69b | 490-69c | 490-69d | 490-69e | 490-69f | 490-69g | 490-69h | 490-69i | 490-70 | 490-71 | 490-72 | 490-73 | 490-74 | 490-75 | 490-76 | 490-77 | 490-78 | 490-79
CERS ID | Facility ID | Organization Name | Organization Code | Facility Name | Facility Street Address | Facility City | Facility ZIP Code | Type of Action | Tank ID # | CERS TankID | Tank Manufacturer | Tank Configuration | Tank Capacity In Gallons | Date UST System Installed | Date UST Permanently Closed | Date Existing UST Discovered | Number of Compartments in the Unit | Additional Description | Tank Use | Specify Other Tank Use | Tank Contents | Specify Other Petroleum | Specify Other Non-Petroleum | Type of Tank | Tank Primary Containment Construction | Other Primary Containment Construction | Tank Secondary Containment Construction | Other Secondary Containment Construction | Audible/ Visual Alarms | Ball Float | Fill Tube Shut-Off Valve | Exempt | Piping Construction | Piping System Type | Primary Containment Construction | Other Primary Containment Construction | Secondary Containment Construction | Other Secondary Containment Construction | Piping/Turbine Containment Sump | Primary Containment Construction | Other Primary Containment Construction | Secondary Containment Construction | Other Secondary Containment Construction | Vent Piping Transition Sumps | Primary Containment Construction | Other Primary Containment Construction | Secondary Containment Construction | Other Secondary Containment Construction | Primary Containment Construction | Other Primary Containment Construction | Secondary Containment Construction | Other Secondary Containment Construction | Spill Bucket Installed | Striker Plate / Bottom Protector Installed | Containment Sump | Construction Type | Construction Material | Other Construction Material | Sacrificial Anode | Impressed Current | Isolation | Date Certified | Applicant Name | Applicant Title | Monitoring Equipment Serviced | Other Frequency of Monitoring Equipment Service | Site Plot Plan Submitted | Continuous Electronic Tank Monitoring | Tank Secondary Containment System | Electronic Monitor Panel Manufacturer | Electronic Monitor Panel Model # | Leak Sensor Manufacturer | Leak Sensor Model # | Automatic Tank Gauging | ATG Panel Manufacturer | ATG Model # | In-Tank Probe Manufacturer | In-tank Probe Model # | Tank Leak Test Frequency | Other Leak Test Frequency | Programmed Tank Tests | Other Programmed Tests | Monthly Statistical Inventory Reconciliation | Weekly Manual Tank Gauge | Tank Gauging Test Period | Tank Integrity Testing | Tank Integrity Testing Frequency | Other Tank Integrity Testing Frequency | Other Monitoring | Specify Other Monitoring | Continuous Monitoring of Piping Secondary Containment | Piping Secondary Containment | Panel Manufacturer | Panel Model # | Leak Sensor Manufacturer | Leak Sensor Model # | Leak Alarm Triggers Automatic Pump Shutdown | Failure/Disconnect Triggers Pump Shutdown | Mechanical Line Leak Detector Performs 3 GPH Leak Test | MLLD Manufacturer | MLLD Model # | Electronic Line Leak Detector Performs 3 GPH Leak Test | ELLD Manufacturer | ELLD Model # | ELLD Programmed In-Line Testing | ELLD Triggers Automatic Pump Shutdown | ELLD Failure/Disconnect Triggers Automatic Shutdown | Pipeline Integrity Testing | Pipeline Integrity Testing Frequency | Other Pipeline Integrity Testing Frequency | Visual Pipeline Monitoring | Visual Pipeline Monitoring Frequency | Suction Piping Meets Exemption Criteria | No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System | Other Pipeline Monitoring | Other Pipeline Monitoring Description | UDC Monitoring | Other UDC Monitoring | UDC Panel Manufacturer | UDC Panel Model # | UDC Leak Sensor Manufacturer | UDC Leak Sensor Model # | Detection of Leak into UDC Triggers Audible and Visual Alarms | UDC Leak Alarm Triggers Automatic Pump Shutdown | Failure/Disconnection of UDC Monitoring System Triggers Automatic Pump Shutdown | UDC Monitoring Stops Flow of Product at Dispenser | UDC Construction | UDC Secondary Containment Monitoring | Leak Within Secondary Containment of UDC Causes Audible and Visual Alarms | ELD Testing | Secondary Containment Testing | Spill Bucket Testing | Alarm Logs | Visual Inspection Records | Tank Integrity Testing Results | SIR Testing Results | Tank Gauging Results | ATG Testing Results | Corrosion Protection Logs | Equipment Maintenance and Calibration Records | Personnel with UST Monitoring Responsibilities are Familiar with Training Documents | UST Monitoring Plan | Operating Manuals | CA UST Regulations | CA UST Law | SWRCB Handbook for Tank Owners - Manual and SIR | SWRCB Publication: Understanding Automatic Tank Gauging Systems | Other Training Documents | Other Training Documents Description | Designated Operator Training | Comments and Additional Information | Name of First Person Having Responsibility | Title of First Person Having Responsibility | Name of Second Person Having Responsibility | Title of Second Person Having Responsibility | Signature Representation | Signature Date | Applicant Name | Applicant Title | Date Submitted to CERS | Date Accepted by Regulator | Regulator Agent Name | Regulator Name | Regulator Type
10030615 | 21-000-601316 | AS Convenience & Energy Inc. | 90379039 | 24/7 Northgate | 930 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 2 | 10030615-002 | Owens Corning | A Stand-alone Tank | 10000 | 1984-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Midgrade Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | MAG 1 | Yes | Yes | No |  |  | Yes | Veeder - Root | VR Series 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder - Root | TLS - 350 | Veeder - Root | 794380-208 | No | Yes | Yes | Yes |  |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel 'Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-04-19 09:25 | 2024-04-19 13:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030615 | 21-000-601316 | AS Convenience & Energy Inc. | 90379039 | 24/7 Northgate | 930 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10030615-001 | Owens Corning | A Stand-alone Tank | 12000 | 1984-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS-350 | Veeder Root | MAG 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS - 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | No | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-04-19 09:25 | 2024-04-19 13:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030615 | 21-000-601316 | AS Convenience & Energy Inc. | 90379039 | 24/7 Northgate | 930 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 4 | 10030615-004 | Owens Corning | A Stand-alone Tank | 10000 | 1984-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder - Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | No | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-04-19 09:25 | 2024-04-19 13:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030615 | 21-000-601316 | AS Convenience & Energy Inc. | 90379039 | 24/7 Northgate | 930 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 3 | 10030615-003 | Owens Corning | A Stand-alone Tank | 8000 | 1984-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | No | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-04-19 09:25 | 2024-04-19 13:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 3 | 10030618-007 | XERXES | A Stand-alone Tank | 12000 | 2021-07-20 |  |  | 1 | T3-DIESEL (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 330020-463 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 330020-463 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-463 & VR-209 SENSORS. VENT & UDC SUMPS MONITORED BY VR-463 & VR-208 SENSORS. ATG SYSTEM WITHIN-TANK VR-MAG PROBE USED FOR INVENTORY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER |  |  |  |  | 2024-05-13 13:20 | 2024-05-15 13:57 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 2 | 10030618-006 | XERXES | A Stand-alone Tank | 15000 | 2021-07-20 |  |  | 1 | T2-SUPREME (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 330020-463 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 330020-463 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-463 & VR-209 SENSORS. VENT & UDC SUMPS MONITORED BY VR-463 & VR-208 SENSORS. ATG SYSTEM WITHIN-TANK VR-MAG PROBE USED FOR INVENTORY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER |  |  |  |  | 2024-05-13 13:20 | 2024-05-15 13:57 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | UST Removal | 3 - (T1) | 10030618-003 | Owens Corning | A Stand-alone Tank | 10000 | 1983-01-01 | 2021-06-29 |  | 1 | Removed this single wall tank on 6/29/2021. Another submittal will be made for the new double wall VPH UST system. - T1-SUPREME (PER VEEDER ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Pressure | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE | RETAIL HES | Annually |  | New Plan Submitted | No | [5 empty] | Yes | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | MAG | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-352 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  | No | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) SUMP MONITORED BY VR-352 SENSOR. AUTOMATIC TANK GAUGING (ATG) SYSTEM USED TO MONITOR SINGLE WALL TANK(S) WITH IN-TANK VEEDER ROOT MAG PROBE & CSLD. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | Station Manager | Station Manager | Assistant Manager | Assistant Manager | Tank Owner/Operator |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | 2022-01-06 14:47 | 2022-02-10 10:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | UST Removal | 1 - (T2) | 10030618-001 | Owens Corning | A Stand-alone Tank | 10000 | 1983-01-01 | 2021-06-29 |  | 1 | Removed this single wall tank on 6/29/2021. Another submittal will be made for the new double wall VPH UST system. - T-2 REGULAR 1 (PER VEEDER ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Pressure | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | Annually |  | New Plan Submitted | No | [5 empty] | Yes | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | MAG | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-352 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  | No | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) SUMP MONITORED BY VR-352 SENSOR. AUTOMATIC TANK GAUGING (ATG) SYSTEM USED TO MONITOR SINGLE WALL TANK(S) WITH IN-TANK VEEDER ROOT MAG PROBE & CSLD. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | Station Manager | Station Manager | Assistant Manager | Assistant Manager | Tank Owner/Operator |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | 2022-01-06 14:47 | 2022-02-10 10:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | UST Removal | 2 - (T4) | 10030618-002 | OWENS CORNING | A Stand-alone Tank | 10000 | 1983-01-01 | 2021-06-29 |  | 1 | Removed this single wall tank on 6/29/2021. Another submittal will be made for the new double wall VPH UST system. - T4-DIESEL (PER VEEDER ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Pressure | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | Annually |  | New Plan Submitted | No | [5 empty] | Yes | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | MAG | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-352 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  | No | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) SUMP MONITORED BY VR-352 SENSOR. AUTOMATIC TANK GAUGING (ATG) SYSTEM USED TO MONITOR SINGLE WALL TANK(S) WITH IN-TANK VEEDER ROOT MAG PROBE & CSLD. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | Station Manager | Station Manager | Assistant Manager | Assistant Manager | Tank Owner/Operator |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | 2022-01-06 14:47 | 2022-02-10 10:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | UST Removal | 4 - (T3) | 10030618-004 | XERXES | A Stand-alone Tank | 10000 | 1987-01-01 | 2021-06-29 |  | 1 | Removed this tank on 6/29/2021. Another submittal will be made for the new double wall VPH UST system. - T-3 REGULAR 2 (PER VEEDER ROOT PROGRAMMING) - AUXILIARY TANK | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Single-walled | Pressure | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | THIS AUXILIARY TANK IS PROTECTED BY THE ELLD ON THE MAIN TANK TURBINE. UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | Station Manager | Station Manager | Assistant Manager | Assistant Manager | Tank Owner/Operator |  | CHARLES BITTLE - 8/21/2015 | RETAIL HES | 2022-01-06 14:47 | 2022-02-10 10:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030618 | 21-000-300036 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 93553 | 949 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10030618-005 | XERXES | A Stand-alone Tank | 20000 | 2021-07-20 |  |  | 1 | T1-REGULAR (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 330020-463 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 330020-463 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-463 & VR-209 SENSORS. VENT & UDC SUMPS MONITORED BY VR-463 & VR-208 SENSORS. ATG SYSTEM WITHIN-TANK VR-MAG PROBE USED FOR INVENTORY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER |  |  |  |  | 2024-05-13 13:20 | 2024-05-15 13:57 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030663 | 21-000-601496 | Matt and Jeff's Fuel 24:7 | 90838336 | Matt and Jeff's Fuel 24:7 | 1515 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10030663-001 | Modern Welding | A Stand-alone Tank | 12000 | 1994-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Steel |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Fiberglass |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | VM1 | Vaporless 99LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nik Zagorov | Designated Operator | Ben V. Shimek | President | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-03-07 15:26 | 2023-03-13 12:06 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030663 | 21-000-601496 | Matt and Jeff's Fuel 24:7 | 90838336 | Matt and Jeff's Fuel 24:7 | 1515 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10030663-003 | Modern Welding | One in a Compartmented Unit | 7000 | 1994-01-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Steel |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Fiberglass |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | MV1 | Vaporless 99LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nik Zagorov | Designated Operator | Ben V. Shimek | President | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-03-07 15:26 | 2023-03-13 12:06 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030663 | 21-000-601496 | Matt and Jeff's Fuel 24:7 | 90838336 | Matt and Jeff's Fuel 24:7 | 1515 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10030663-002 |  | One in a Compartmented Unit | 5000 | 1994-01-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Steel |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Fiberglass |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | VM1 | Vaporless 99LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nik Zagorov | Designated Operator | Ben V. Shimek | President | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-03-07 15:26 | 2023-03-13 12:06 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030669 | 21-000-601222 | Faizan Corporation | 90427900 | Faizan Corporation | 170 Merrydale Road | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10030669-001 | Unknown | A Stand-alone Tank | 10000 | 1973-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Haji Alam | President | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Haji Alam | President | Deepak Banya | Manager | Facility Owner/Operator |  | Haji Alam | President | 2024-04-22 17:57 | 2024-04-24 10:19 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030669 | 21-000-601222 | Faizan Corporation | 90427900 | Faizan Corporation | 170 Merrydale Road | San Rafael | 94903 | Confirmed/Updated Information | 3 | 10030669-003 | Unknown | A Stand-alone Tank | 10000 | 1973-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Haji Alam | President | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Haji Alam | President | Deepak Banya | Manager | Facility Owner/Operator |  | Haji Alam | President | 2024-04-22 17:57 | 2024-04-24 10:19 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030669 | 21-000-601222 | Faizan Corporation | 90427900 | Faizan Corporation | 170 Merrydale Road | San Rafael | 94903 | Confirmed/Updated Information | 2 | 10030669-002 | Unknown | A Stand-alone Tank | 6000 | 1973-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Haji Alam | President | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag 1 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Haji Alam | President | Deepak Banya | Manager | Facility Owner/Operator |  | Haji Alam | President | 2024-04-22 17:57 | 2024-04-24 10:19 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030819 | 21-000-300104 | Marin Sanitary Service | 90097396 | Marin Sanitary Service | 1050 Andersen Drive | San Rafael | 94901 | UST Permanent Closure on Site | 2 | 10030819-002 | unknown | A Stand-alone Tank | 10000 | 1975-01-01 | 2019-01-03 | 1999-01-01 | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | 23 CCR §2636(a)(3) Suction | Steel |  | None |  | None | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | Yes | No | No |  | Joseph Garbarino | vice president | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder root | Gilbarco EMC | Veeder root | MAG-1 | Monthly |  | 0.1 GPH |  | No | No |  | No |  |  | No |  | No | [7 empty] | No |  |  | Yes | Incon | TS-LLD | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Beaudreau | 404 | Beaudreau | 404/406 | No | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Ron Piombo | vice president Facilities | Rudy Tescallo | shop foreman | Authorized Representative of Owner |  | Joseph Garbarino | vice president | 2023-01-10 11:38 | 2023-01-31 22:27 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10030819 | 21-000-300104 | Marin Sanitary Service | 90097396 | Marin Sanitary Service | 1050 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10030819-001 | Owens Corning | A Stand-alone Tank | 10000 | 1975-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | 23 CCR §2636(a)(3) Suction | Steel |  | None |  | None | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: Yes; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Joseph Garbarino; UST Tank Certification / Applicant Information 472: vice president; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: Veeder-Root; Automatic Tank Gauging 490-13: TLS-350; Automatic Tank Gauging 490-14: Veeder-Root; Automatic Tank Gauging 490-15: PA 02650960100; Automatic Tank Gauging 490-16: Monthly; Automatic Tank Gauging 490-18: 0.1 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Electronic Stand-alone; Under Dispenser Containment (UDC) Monitoring 490-57: Beaudreau; Under Dispenser Containment (UDC) Monitoring 490-58: 404/406; Under Dispenser Containment (UDC) Monitoring 490-59: Yes; Under Dispenser Containment (UDC) Monitoring 490-60: Yes; Under Dispenser Containment (UDC) Monitoring 490-61: Yes; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: Yes; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: No sumps; Personnel Responsibilities 490-72: Cliff Spencer; Personnel Responsibilities 490-73: Assistant Shop Foreman; Personnel Responsibilities 490-74: Justin Wilcock; Personnel Responsibilities 490-75: Director of Operations; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Joseph Garbarino; UST Monitoring Plan Certification / Applicant Information 490-79: vice president | 2023-01-10 11:38 | 2023-01-31 22:27 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10030819 | 21-000-300104 | Marin Sanitary Service | 90097396 | Marin Sanitary Service | 1050 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10030819-003 | Owens Corning | A Stand-alone Tank | 10000 | 1981-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Pressure | Steel |  | None |  | None | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | Yes | No | No |  | Joseph Garbarino | vice president | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder root | TLS-350 | Veeder root | PA 02650960100 | Monthly |  | 0.1 GPH |  | No | No |  | No |  |  | No |  | No | [7 empty] | No |  |  | Yes | Incon | TS-LLD | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  |  | Beaudreau | 404/406 | No | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | [8 empty] | Yes | No sumps | Cliff Spencer | Assistant Shop Foreman | Justin Wilcock | Director of Operations | Authorized Representative of Owner |  | Joseph Garbarino | vice president | 2023-01-10 11:38 | 2023-01-31 22:27 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10030891 | 21-000-300133 | Union 76 Of Marin | 90852535 | Union 76 Of Marin | 831 Francisco Boulevard East | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10030891-002 | TRUSCO | A Stand-alone Tank | 10000 | 1992-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Fiberglass |  | Double-walled | Fiberglass |  | Rigid Plastic |  | Rigid Plastic |  | Rigid Plastic |  | Yes | No | No | Single-walled | Steel |  | No | No | Yes |  | PETER JIZRAWI | OWNER | Annually |  | Site Plan Previously Submitted | Yes | Dry | VEEDER ROOT | TSL350 | VEEDER ROOT | VR420 | Yes | VEEDER ROOT | TSL350 | VEEDER ROOT | MAG PROBE | Continuous |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TSL350 | VEEDER ROOT | VR208 | Yes | Yes | Yes | Franklin Fueling Systems | FE-Petro | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TSL350 | VEEDER ROOT | VRT208 | Yes | Yes | Yes | Yes | Single-walled | Liquid |  | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | [8 empty] | No |  | PETER JIZRAWI | OWNER | GEORGE ANTAR | GM | Tank Owner/Operator |  | PETER JIZRAWI | OWNER | 2024-01-04 10:57 | 2024-01-04 12:19 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030891 | 21-000-300133 | Union 76 Of Marin | 90852535 | Union 76 Of Marin | 831 Francisco Boulevard East | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10030891-003 | TRUSCO | A Stand-alone Tank | 10000 | 1992-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Fiberglass |  | Double-walled | Fiberglass |  | Rigid Plastic |  | Rigid Plastic |  | Rigid Plastic |  | Yes | No | No | Single-walled | Steel |  | No | No | Yes |  | PETER JIZRAWI | OWNER | Annually |  | Site Plan Previously Submitted | Yes | Dry | VEEDER ROOT | TSL350 | VEEDER ROOT | VR420 | Yes | VEEDER ROOT | TSL350 | VEEDER ROOT | MAG PROBE | Continuous |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TSL350 | VEEDER ROOT | VR208 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TSL350 | VEEDER ROOT | VRT208 | Yes | Yes | Yes | Yes | Single-walled | Liquid | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | [8 empty] | No |  | PETER JIZRAWI | OWNER | GEORGE ANTAR | GM | Tank Owner/Operator |  | PETER JIZRAWI | OWNER | 2024-01-04 10:57 | 2024-01-04 12:19 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030891 | 21-000-300133 | Union 76 Of Marin | 90852535 | Union 76 Of Marin | 831 Francisco Boulevard East | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10030891-001 | TRUSCO | A Stand-alone Tank | 10000 | 1992-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Fiberglass |  | Double-walled | Fiberglass |  | Rigid Plastic |  | Rigid Plastic |  | Rigid Plastic |  | Yes | No | No | Single-walled | Steel |  | No | No | Yes |  | PETER JIZRAWI | OWNER | Annually |  | Site Plan Previously Submitted | Yes | Dry | VEEDER ROOT | TSL350 | VEEDER ROOT | VR420 | Yes | VEEDER ROOT | TSL350 | VEEDER ROOT | MAG PROBE | Continuous |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TSL350 | VEEDER ROOT | VR208 | Yes | Yes | Yes | Vaporless | LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TSL350 | VEEDER ROOT | VRT208 | Yes | Yes | Yes | Yes | Single-walled | Liquid | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | [8 empty] | No |  | PETER JIZRAWI | OWNER | GEORGE ANTAR | GM | Tank Owner/Operator |  | PETER JIZRAWI | OWNER | 2024-01-04 10:57 | 2024-01-04 12:19 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10030894 | 21-000-300134 | Peter's Beacon | 90097696 | Peter's Beacon | 108 Bellam Boulevard | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10030894-002 | Modern | A Stand-alone Tank | 12000 | 2003-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Samir Jizrawi | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS350 | Veeder Root | VR420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS350 | Veeder Root | VR208 |  |  | No |  |  | Yes | Veeder Root | VR Series 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS350 | Veeder Root | VR208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Samir Jizrawi | Owner | Soraya Jizrawi | Office Manager | Facility Owner/Operator |  | Samir Jizrawi | owner | 2023-05-12 13:12 | 2023-09-14 11:07 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030894 | 21-000-300134 | Peter's Beacon | 90097696 | Peter's Beacon | 108 Bellam Boulevard | San Rafael | 94901 | Renewal Permit | 1 | 10030894-001 | Modern | A Stand-alone Tank | 12000 | 2003-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Steel |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | No |  | Samir Jizrawi | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS350 | Veeder Root | VR420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS350 | Veeder Root | VR208 | Yes | Yes | No |  |  | Yes | Veeder Root | VR Series 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS350 | Veeder Root | VR208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Samir Jizrawi | Owner | Soraya Jizrawi | Office Manager | Facility Owner/Operator |  | Samir Jizrawi | owner | 2023-05-12 13:12 | 2023-09-14 11:07 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10030894 | 21-000-300134 | Peter's Beacon | 90097696 | Peter's Beacon | 108 Bellam Boulevard | San Rafael | 94901 | Renewal Permit | 3 | 10030894-003 | Modern | A Stand-alone Tank | 12000 | 2003-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Samir Jizrawi | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS350 | Veeder Root | VR420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS350 | Veeder Root | VR208 | Yes | Yes | No |  |  | Yes | Veeder Root | VR Series 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS350 | Veeder Root | VR208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Samir Jizrawi | Owner | Soraya Jizrawi | Office Manager | Facility Owner/Operator |  | Samir Jizrawi | owner | 2023-05-12 13:12 | 2023-09-14 11:07 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031020 | 21-000-300178 | Central Marin Sanitation Agency | 90098158 | Central Marin Sanitation Agency | 1301 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10031020-002 | Xerxes | A Stand-alone Tank | 6000 | 1996-01-01 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Fiberglass; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Mary Jo Ramey; UST Tank Certification / Applicant Information 472: Environmental Service Analyst; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Omntec; Continuous Electronic Tank Monitoring 490-8: OEL8000; Continuous Electronic Tank Monitoring 490-9: Omntec; Continuous Electronic Tank Monitoring 490-10: BX-LWF; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Omntec; Continuous Monitoring of Piping Secondary Containment 490-31: OEL8000; Continuous Monitoring of Piping Secondary Containment 490-32: Omntec; Continuous Monitoring of Piping Secondary Containment 490-33: BX-LS; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Continuous; Under Dispenser Containment (UDC) Monitoring 490-55: Omntec; Under Dispenser Containment (UDC) Monitoring 490-56: OEL8000; Under Dispenser Containment (UDC) Monitoring 490-57: Omntec; Under Dispenser Containment (UDC) Monitoring 490-58: BX-LS; Under Dispenser Containment (UDC) Monitoring 490-59: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: No; Personnel Responsibilities 490-72: Peter Kistenmacher; Personnel Responsibilities 490-73: Technical Services Manager; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Mary Jo Ramey; UST Monitoring Plan Certification / Applicant Information 490-79: Environment Services Analyst | 2023-12-01 06:23 | 2023-12-27 10:12 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031020 | 21-000-300178 | Central Marin Sanitation Agency | 90098158 | Central Marin Sanitation Agency | 1301 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10031020-001 | Trusco | A Stand-alone Tank | 2000 | 1999-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Fiberglass; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Mary Jo Ramey; UST Tank Certification / Applicant Information 472: Environmental Services Analyst; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-300C; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-300C; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Continuous; Under Dispenser Containment (UDC) Monitoring 490-55: Veeder-Root; Under Dispenser Containment (UDC) Monitoring 490-56: TLS-300C; Under Dispenser Containment (UDC) Monitoring 490-57: Veeder-Root; Under Dispenser Containment (UDC) Monitoring 490-58: 208; Under Dispenser Containment (UDC) Monitoring 490-59: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: No; Personnel Responsibilities 490-72: Peter Kistenmacher; Personnel Responsibilities 490-73: Technical Services Manager; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Mary Jo Ramey; UST Monitoring Plan Certification / Applicant Information 490-79: Environmental Services Analyst | 2023-12-01 06:23 | 2023-12-27 10:12 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031029 | 21-000-300181 | Kaiser Permanente Medical Center | 90098194 | Kaiser Permanente San Rafael Medical Center | 99 Montecillo Road | San Rafael | 94903 | Confirmed/Updated Information | 3 | 10031029-003 | XERXES | A Stand-alone Tank | 6000 | 2014-06-30 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: RICHARD NEWTON; UST Tank Certification / Applicant Information 472: CHIEF ENGINEER; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Liquid-Filled; Continuous Electronic Tank Monitoring 490-7: FRANKLIN FUELING SYSTEMS; Continuous Electronic Tank Monitoring 490-8: TS-550 EVO; Continuous Electronic Tank Monitoring 490-9: FRANKLIN FUELING SYS; Continuous Electronic Tank Monitoring 490-10: TS-HIS; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Under Vacuum; Continuous Monitoring of Piping Secondary Containment 490-30: FRANKLIN FUELING SYSTEMS; Continuous Monitoring of Piping Secondary Containment 490-31: TS-550 EVO; Continuous Monitoring of Piping Secondary Containment 490-32: FRANKLIN FUELING SYS; Continuous Monitoring of Piping Secondary Containment 490-33: TS-SCCM; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: Yes; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-40: Franklin Fueling; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-41: TS-LS500; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-43: Yes; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-44: Yes; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: ATG PROBE USED FOR OVERFILL & INVENTORY PURPOSES. ALL SUMPS CONTINUOUSLY MONITORED BY BRINE SENSOR TSP-UHS. ALL LINES CONTINUOUSLY MONITORED BY VACCUM SENSOR TS-SCCM.; Personnel Responsibilities 490-72: VINCENT MORRIS; Personnel Responsibilities 490-73: CHIEF ENGINEER; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: RICHARD NEWTON; UST Monitoring Plan Certification / Applicant Information 490-79: CHIEF ENGINEER | 2024-04-10 15:09 | 2024-06-07 12:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031029 | 21-000-300181 | Kaiser Permanente Medical Center | 90098194 | Kaiser Permanente San Rafael Medical Center | 99 Montecillo Road | San Rafael | 94903 | UST Removal | 2 | 10031029-002 | KAEMPEN | A Stand-alone Tank | 7500 | 1988-01-01 | 2022-07-24 |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: RICHARD NEWTON; UST Tank Certification / Applicant Information 472: CHIEF ENGINEER; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: VEEDER ROOT; Automatic Tank Gauging 490-13: TLS-350; Automatic Tank Gauging 490-14: VEEDER ROOT; Automatic Tank Gauging 490-15: MAG PLUS; Automatic Tank Gauging 490-16: Monthly; Automatic Tank Gauging 490-18: 0.2 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: RICHARD NEWTON; Personnel Responsibilities 490-73: CHIEF ENGINEER; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: RICHARD NEWTON; UST Monitoring Plan Certification / Applicant Information 490-79: CHIEF ENGINEER | 2023-04-05 15:32 | 2023-04-11 16:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031029 | 21-000-300181 | Kaiser Permanente Medical Center | 90098194 | Kaiser Permanente San Rafael Medical Center | 99 Montecillo Road | San Rafael | 94903 | UST Removal | 1 | 10031029-001 | KAEMPEN | A Stand-alone Tank | 7500 | 1988-01-01 | 2022-07-24 |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: RICHARD NEWTON; UST Tank Certification / Applicant Information 472: CHIEF ENGINEER; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: VEEDER ROOT; Automatic Tank Gauging 490-13: TLS-350; Automatic Tank Gauging 490-14: VEEDER ROOT; Automatic Tank Gauging 490-15: MAG PLUS; Automatic Tank Gauging 490-16: Monthly; Automatic Tank Gauging 490-18: 0.2 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: RICHARD NEWTON; Personnel Responsibilities 490-73: CHIEF ENGINEER; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: RICHARD NEWTON; UST Monitoring Plan Certification / Applicant Information 490-79: CHIEF ENGINEER | 2023-04-05 15:32 | 2023-04-11 16:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031032 | 21-000-300182 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 06157 | 1401 2nd St | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10031032-001 | JOOR | A Stand-alone Tank | 12000 | 1992-11-01 |  |  | 1 | MAIN | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Other |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | PLLD (8484) |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | ATG PROBE USED FOR INVENTORY PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208. | RANDALL BROWN | HSSE&C ADVISOR | BRENDA DONOVAN | HSSE&C ADVISOR | Authorized Representative of Owner |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | 2024-07-01 15:54 | 2024-07-10 12:13 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031032 | 21-000-300182 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 06157 | 1401 2nd St | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10031032-003 | JOOR | A Stand-alone Tank | 12000 | 1992-11-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Other |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | PLLD (8484) |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | ATG PROBE USED FOR INVENTORY PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208. | RANDALL BROWN | HSSE&C ADVISOR | BRENDA DONOVAN | HSSE&C ADVISOR | Authorized Representative of Owner |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | 2024-07-01 15:54 | 2024-07-10 12:13 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031032 | 21-000-300182 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 06157 | 1401 2nd St | San Rafael | 94901 | Confirmed/Updated Information | 4 | 10031032-004 | JOOR | A Stand-alone Tank | 500 | 1992-11-01 |  |  | 1 |  | Hazardous Waste (includes used oil) |  | Used Oil |  |  | Double Wall | Steel |  | Other |  | Yes | No | No | No | Single-walled | Gravity | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: JENNIFER M. SOSIN; UST Tank Certification / Applicant Information 472: RETAIL COMPLIANCE MANAGER; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-10: 794380-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: ATG PROBE USED FOR INVENTORY AND OVERFILL PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208.; Personnel Responsibilities 490-72: RANDALL BROWN; Personnel Responsibilities 490-73: HSSE&C ADVISOR; Personnel Responsibilities 490-74: BRENDA DONOVAN; Personnel Responsibilities 490-75: HSSE&C ADVISOR; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: JENNIFER M. SOSIN; UST Monitoring Plan Certification / Applicant Information 490-79: RETAIL COMPLIANCE MANAGER | 2024-07-01 15:54 | 2024-07-10 12:13 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031032 | 21-000-300182 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 06157 | 1401 2nd St | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10031032-002 | JOOR | A Stand-alone Tank | 12000 | 1992-11-01 |  |  | 1 | AUX | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Other |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | No |  | No | No | Yes |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | ATG PROBE USED FOR INVENTORY PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208. | RANDALL BROWN | HSSE&C ADVISOR | BRENDA DONOVAN | HSSE&C ADVISOR | Authorized Representative of Owner |  | JENNIFER M. SOSIN | RETAIL COMPLIANCE MANAGER | 2024-07-01 15:54 | 2024-07-10 12:13 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031083 | 21-000-300200 | PG&E | 90000226 | PG&E - San Rafael Service Center | 1220 Andersen Drive | San Rafael | 94901 | UST Removal | Unleaded | 10031083-001 | Modern Welding | A Stand-alone Tank | 25000 | 1987-01-01 | 2017-03-09 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Other |  | Yes | No | Yes | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Cara Bateman | Senior Environmental Specialist | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-205 | No | No | No |  |  | No | [5 empty] | Yes | Other |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Cara Bateman | Senior Environmental Field Specialist |  |  | Tank Owner/Operator |  | Cara Bateman | Senior Environmental Specialist | 2017-03-31 11:07 | 2017-05-23 13:59 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031083 | 21-000-300200 | PG&E | 90000226 | PG&E - San Rafael Service Center | 1220 Andersen Drive | San Rafael | 94901 | UST Removal | Diesel | 10031083-002 | Modern Welding | A Stand-alone Tank | 8000 | 1987-01-01 | 2017-03-02 |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Other |  | Yes | No | Yes | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Cara Bateman | Senior Environmental Specialist | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-205 | No | No | No |  |  | No | [5 empty] | Yes | Other |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Cara Bateman | Senior Environmental Field Specialist |  |  | Tank Owner/Operator |  | Cara Bateman | Senior Environmental Specialist | 2017-03-31 11:07 | 2017-05-23 13:59 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031098 |  | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | Pacific Bell W3084 | 2000 Bayhills Dr | San Rafael | 94903 | UST Removal | W3084U001 | 10031098-001 | Modern Welding | A Stand-alone Tank | 3000 | 1993-01-01 | 2012-06-07 |  | 1 | Researched records of actual date tank was removed. | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Steven J Hall; UST Tank Certification / Applicant Information 472: Manager, EH&S; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-350 Plus; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: (L1) 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350 Plus; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: Fill Tube Shut-Off Valve is the Primary Overfill Protection Device on this system, set to activate at 95% of tank capacity. (L2) Fill Sump (L4) Transition Box & (L5) Pipe Tray Sensors (3) - 794380-208; Personnel Responsibilities 490-72: Tait Environmental Services; Personnel Responsibilities 490-73: AT&T Authorized Vendor (Contact List Available Upo; Personnel Responsibilities 490-74: AT&T Environment Health & Safety; Personnel Responsibilities 490-75: Call Center; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Steven J Hall; UST Monitoring Plan Certification / Applicant Information 490-79: Manager, EH&S | 2022-11-22 05:45 | 2022-11-29 15:02 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031515 | 21-000-300353 | Circle K Stores Inc. | 90141874 | Circle K Stores, Store #5784 | 981 Francisco Boulevard East | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10031515-002 | Owens-Corning | A Stand-alone Tank | 10000 | 1994-01-01 |  |  | 1 | 91 Product UST. | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | Robert Velasco | Agent for Circle K | Annually |  | New Plan Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | Fe Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | Environmental Records Binder | Yes |  | Reyna Mendez | Environmental Compliance Specialist | Adrienne Knoblock | Environmental Compliance Manager | Authorized Representative of Owner |  | Robert Velasco | Agent for Circle K | 2024-02-06 10:18 | 2024-03-12 10:15 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031515 | 21-000-300353 | Circle K Stores Inc. | 90141874 | Circle K Stores, Store #5784 | 981 Francisco Boulevard East | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10031515-001 | Owens-Corning | A Stand-alone Tank | 10000 | 1994-01-01 |  |  | 1 | Diesel Product UST. | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | Robert Velasco | Agent for Circle K | Annually |  | New Plan Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | VMI | 99LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | Environmental Records Binder | Yes |  | Reyna Mendez | Environmental Compliance Specialist | Adrienne Knoblock | Environmental Compliance Manager | Authorized Representative of Owner |  | Robert Velasco | Agent for Circle K | 2024-02-06 10:18 | 2024-03-12 10:15 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031515 | 21-000-300353 | Circle K Stores Inc. | 90141874 | Circle K Stores, Store #5784 | 981 Francisco Boulevard East | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10031515-003 | Owens-Corning | A Stand-alone Tank | 12000 | 1994-01-01 |  |  | 1 | 87 Product UST. | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | Robert Velasco | Agent for Circle K | Annually |  | New Plan Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | Vaporless | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | Environmental Records Binder | Yes |  | Reyna Mendez | Environmental Compliance Specialist | Adrienne Knoblock | Environmental Compliance Manager | Authorized Representative of Owner |  | Robert Velasco | Agent for Circle K | 2024-02-06 10:18 | 2024-03-12 10:15 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031551 | 21-000-601073 | County of Marin: Facilities Planning | 90390964 | Sares Regis Group of Northern California | 1600 Los Gamos | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10031551-001 | Modern Welding | A Stand-alone Tank | 8000 | 1999-01-01 |  | 1999-01-01 | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | None | None |  | None |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Incon; Continuous Electronic Tank Monitoring 490-8: TS 1000; Continuous Electronic Tank Monitoring 490-9: Incon; Continuous Electronic Tank Monitoring 490-10: TSP ULS; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Incon; Continuous Monitoring of Piping Secondary Containment 490-31: TS-1000; Continuous Monitoring of Piping Secondary Containment 490-32: Incon; Continuous Monitoring of Piping Secondary Containment 490-33: TSP-ULS; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Kathy Koaleff; Personnel Responsibilities 490-73: Property Manager; Personnel Responsibilities 490-74: Robert Hollingsworth; Personnel Responsibilities 490-75: Chief Engineer | 2022-12-14 14:08 | 2022-12-19 15:44 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031569 | 21-000-300371 | Terra Linda 76 & Pro Car Wash | 90100174 | Terra Linda 76 & Pro Car Wash | 921 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10031569-001 | Modern Welding | A Stand-alone Tank | 15000 | 1999-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Other |  | No | Yes | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | Yes |  | Parminder Singh Grewal | Tank Operator | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | STP-MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Parminder Singh Grewal | Tank Operator | Malkeet Grewal | Wife | Tank Owner/Operator |  | Parminder Singh Grewal | Tank Operator | 2023-11-09 15:15 | 2023-11-09 15:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031569 | 21-000-300371 | Terra Linda 76 & Pro Car Wash | 90100174 | Terra Linda 76 & Pro Car Wash | 921 Del Presidio Boulevard | San Rafael | 94903 | Confirmed/Updated Information | 2 | 10031569-002 | Modern Welding | A Stand-alone Tank | 12000 | 1999-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Other |  | No | Yes | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | Yes |  | Parminder Singh Grewal | Tank Operator | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Vaporless | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Parminder Singh Grewal | Tank Operator | Malkeet Grewal | Wife | Tank Owner/Operator |  | Parminder Singh Grewal | Tank Operator | 2023-11-09 15:15 | 2023-11-09 15:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031590 | 21-000-300378 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 1011 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | UL234038 | 10031590-003 | K&T Steel | A Stand-alone Tank | 20000 | 1991-12-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | Fiberglass |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: David Denning; UST Tank Certification / Applicant Information 472: EH&S Specialist; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: 350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: 99 LD-2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: Tank ID #3; Personnel Responsibilities 490-72: Epic Compliance; Personnel Responsibilities 490-73: UST Designated Operator; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: David Denning; UST Monitoring Plan Certification / Applicant Information 490-79: EH&S Specialist | 2023-05-17 09:43 | 2023-05-17 16:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031590 | 21-000-300378 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 1011 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | UL234037 | 10031590-002 | K&T Steel | A Stand-alone Tank | 20000 | 1991-12-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | Fiberglass |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Karen Shelar; UST Tank Certification / Applicant Information 472: EH&S Specialist; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: 350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: 99 LD-2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: Tank ID #2; Personnel Responsibilities 490-72: Epic Compliance; Personnel Responsibilities 490-73: UST Designated Operator; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Karen Shelar; UST Monitoring Plan Certification / Applicant Information 490-79: EH&S Specialist | 2023-05-17 09:43 | 2023-05-17 16:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031590 | 21-000-300378 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 1011 Andersen Drive | San Rafael | 94901 | Confirmed/Updated Information | UL234036 | 10031590-001 | K&T Steel | A Stand-alone Tank | 20000 | 1991-12-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | Fiberglass |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Karen Shelar; UST Tank Certification / Applicant Information 472: EH&S Specialist; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: 350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: 99 LD-2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: Tank ID #1; Personnel Responsibilities 490-72: Epic Compliance; Personnel Responsibilities 490-73: UST Designated Operator; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Karen Shelar; UST Monitoring Plan Certification / Applicant Information 490-79: EH&S Specialist | 2023-05-17 09:43 | 2023-05-17 16:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031656 | 21-000-300403 | GAWFCO Enterprises, Inc. | 90365647 | San Rafael Valero | 475 Third Street | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10031656-001 | Xerxes | A Stand-alone Tank | 15000 | 1998-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Mohammed N. Ahmadi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Nick Ahmadi | Co-Dealer | Nader Ahmadi | Co-Dealer | Tank Owner/Operator |  | Mohammed N. Ahmadi | President | 2023-11-07 12:01 | 2024-02-07 15:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031656 | 21-000-300403 | GAWFCO Enterprises, Inc. | 90365647 | San Rafael Valero | 475 Third Street | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10031656-002 | Xerxes | One in a Compartmented Unit | 8000 | 1998-01-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Mohammed N. Ahmadi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Nick Ahmadi | Co-Dealer | Nader Ahmadi | Co-Dealer | Tank Owner/Operator |  | Mohammed N. Ahmadi | President | 2023-11-07 12:01 | 2024-02-07 15:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031656 | 21-000-300403 | GAWFCO Enterprises, Inc. | 90365647 | San Rafael Valero | 475 Third Street | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10031656-003 | Xerxes | One in a Compartmented Unit | 12000 | 1998-01-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Mohammed N. Ahmadi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Nick Ahmadi | Co-Dealer | Nader Ahmadi | Co-Dealer | Tank Owner/Operator |  | Mohammed N. Ahmadi | President | 2023-11-07 12:01 | 2024-02-07 15:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10031959 | 21-000-300524 | Salkhi Family Holdings Inc. | 90130033 | San Rafael Chevron | 440 Third Street | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10031959-001 | TRUSCO | A Stand-alone Tank | 20000 | 2000-09-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-12-29 10:56 | 2024-04-17 18:37 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031959 | 21-000-300524 | Salkhi Family Holdings Inc. | 90130033 | San Rafael Chevron | 440 Third Street | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10031959-002 | TRUSCO | One in a Compartmented Unit | 12000 | 2000-09-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-12-29 10:56 | 2024-04-17 18:37 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031959 | 21-000-300524 | Salkhi Family Holdings Inc. | 90130033 | San Rafael Chevron | 440 Third Street | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10031959-003 | TRUSCO | One in a Compartmented Unit | 8000 | 2000-09-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-12-29 10:56 | 2024-04-17 18:37 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10031965 | 21-000-600001 | Salkhi Family Holdings Inc. | 90130033 | Novato Chevron | 7474 Redwood Boulevard | Novato | 94945 | Confirmed/Updated Information | 3 | 10031965-003 | Trusco | A Stand-alone Tank | 10000 | 1992-04-21 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-205 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS- 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-10-13 10:14 | 2023-11-09 13:55 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10031965 | 21-000-600001 | Salkhi Family Holdings Inc. | 90130033 | Novato Chevron | 7474 Redwood Boulevard | Novato | 94945 | Confirmed/Updated Information | 2 | 10031965-002 | Trusco | A Stand-alone Tank | 8000 | 1992-04-21 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-205 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS- 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-10-13 10:14 | 2023-11-09 13:55 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10031965 | 21-000-600001 | Salkhi Family Holdings Inc. | 90130033 | Novato Chevron | 7474 Redwood Boulevard | Novato | 94945 | Confirmed/Updated Information | 1 | 10031965-001 | Trusco | A Stand-alone Tank | 10000 | 1992-04-21 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-10-13 10:14 | 2023-11-09 13:55 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10031965 | 21-000-600001 | Salkhi Family Holdings Inc. | 90130033 | Novato Chevron | 7474 Redwood Boulevard | Novato | 94945 | Confirmed/Updated Information | 4 | 10031965-004 | Trusco | A Stand-alone Tank | 8000 | 1992-04-21 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-10-13 10:14 | 2023-11-09 13:55 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10031971 | 21-000-600004 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 00524 | 789 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10031971-001 | XERXES | A Stand-alone Tank | 20000 | 2001-09-05 |  |  | 1 | MAIN | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | Annually |  | New Plan Submitted | Yes | Dry | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | PLLD (8484) |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | ATG PROBE USED FOR INVENTORY PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208. | KIMBERLY MEDICUS | HSSE&C ADVISOR | RANDALL BROWN | AREA MAINTENANCE MANAGER | Authorized Representative of Owner |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | 2023-12-29 09:16 | 2024-01-10 00:06 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031971 | 21-000-600004 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 00524 | 789 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10031971-002 | XERXES | One in a Compartmented Unit | 10000 | 2001-09-05 |  |  | 2 | SIPHON | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | Annually |  | New Plan Submitted | Yes | Dry | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | No |  | No | No | Yes |  | Continuous |  | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | ATG PROBE USED FOR INVENTORY PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208. | KIMBERLY MEDICUS | HSSE&C ADVISOR | RANDALL BROWN | AREA MAINTENANCE MANAGER | Authorized Representative of Owner |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | 2023-12-29 09:16 | 2024-01-10 00:06 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10031971 | 21-000-600004 | BP PRODUCTS NORTH AMERICA, INC. | 90135877 | ARCO 00524 | 789 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10031971-003 | XERXES | One in a Compartmented Unit | 12000 | 2001-09-05 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | Annually |  | New Plan Submitted | Yes | Dry | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794390-409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | PLLD (8484) |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | ATG PROBE USED FOR INVENTORY PURPOSES. FILL SUMP MONITORED BY VEEDER ROOT 794380-208. | KIMBERLY MEDICUS | HSSE&C ADVISOR | RANDALL BROWN | AREA MAINTENANCE MANAGER | Authorized Representative of Owner |  | SARAH SAMUELS | RETAIL COMPLIANCE COORDINATOR | 2023-12-29 09:16 | 2024-01-10 00:06 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032106 | 21-000-600061 | Gas & Shop | 90102316 | San Anselmo Gas & Shop | 750 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 2 Premium | 10032106-002 | MODERN WELDING | A Stand-alone Tank | 10140 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Rigid Plastic |  | Rigid Plastic |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Rigid Plastic |  | No | No | Yes |  | Jack Winner | Environmental Compliance | Annually |  | New Plan Submitted | Yes | Dry | Gilbarco | Environmental Management Console | Veeder-Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Gilbarco | Environmental Management Console | Veeder-Root | 794380-208 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  |  | Franklin Fueling | S404 | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Kesh Prasad | General Manager | Jack Winner | Environmental Compliance | Authorized Representative of Owner |  | Jack Winner | Environmental Compliance | 2024-02-19 13:02 | 2024-02-21 13:27 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032106 | 21-000-600061 | Gas & Shop | 90102316 | San Anselmo Gas & Shop | 750 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 3 # Regular | 10032106-003 | MODERN WELDING | A Stand-alone Tank | 10140 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Rigid Plastic |  | Rigid Plastic |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Rigid Plastic |  | No | No | Yes |  | Jack Winner | Environmental Compliance | Annually |  | New Plan Submitted | Yes | Dry | Gilbarco | Environmental Management Console | Veeder-Root | 794390-420 | Yes | Gilbarco | mag | Veeder Root | mag |  |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | Gilbarco | Environmental Management Console | Veeder-Root | 794380-208 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  |  | Franklin Fueling | S404 | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Kesh Prasad | General Manager | Jack Winner | Environmental Compliance | Authorized Representative of Owner |  | Jack Winner | Environmental Compliance | 2024-02-19 13:02 | 2024-02-21 13:27 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032106 | 21-000-600061 | Gas & Shop | 90102316 | San Anselmo Gas & Shop | 750 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 1 Regular | 10032106-001 | MODERN WELDING | A Stand-alone Tank | 12141 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Rigid Plastic |  | Rigid Plastic |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Rigid Plastic |  | No | No | Yes |  | Jack Winner | Environmental Compliance | Annually |  | New Plan Submitted | Yes | Dry | Gilbarco | Environmental Management Console | Veeder-Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Gilbarco | Environmental Management Console | Veeder-Root | 794380-208 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  |  | Franklin Fueling | S404 | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Kesh Prasad | General Manager | Jack Winner | Environmental Compliance | Authorized Representative of Owner |  | Jack Winner | Environmental Compliance | 2024-02-19 13:02 | 2024-02-21 13:27 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | Confirmed/Updated Information | 4 | 10032109-007 | Xerxes | One in a Compartmented Unit | 8000 | 2022-12-14 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 (shared with 91 tank) | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/330020-480 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes | Fill Sump Sensors and Vents 794380-280/794380-304 | Arash Salkhi | President | Samuel 'Sammy" Spencer | District Manager |  |  |  |  | 2023-11-28 08:36 | 2024-01-08 11:07 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10032109-004 | Xerxes | One in a Compartmented Unit | 12000 | 2022-12-14 |  |  | 2 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/330020-485 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes | Fill Sump Sensors and Vents 794380-280/794380-304 | Arash Salkhi | President | Samuel 'Sammy" Spencer | District Manager |  |  |  |  | 2023-11-28 08:36 | 2024-01-08 11:07 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10032109-006 | Xerxes | One in a Compartmented Unit | 12000 | 2022-12-14 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/330020-480 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes | Fill Sump Sensors and Vents 794380-280/794380-304 | Arash Salkhi | President | Samuel 'Sammy" Spencer | District Manager |  |  |  |  | 2023-11-28 08:36 | 2024-01-08 11:07 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10032109-005 | Xerxes | One in a Compartmented Unit | 8000 | 2022-12-14 |  |  | 2 |  | Motor Vehicle Fueling |  | E85 |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 (shared with 87 tank) | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-323/794380-304/330020-480 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-323/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes | Fill Sump 794380-323/794380-304, Vent 794380-208-/794380-304Dispenser 3/4 has E85 | Arash Salkhi | President | Samuel 'Sammy" Spencer | District Manager |  |  |  |  | 2023-11-28 08:36 | 2024-01-08 11:07 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | UST Removal | 3 | 10032109-003 | Xeres | A Stand-alone Tank | 10000 | 1982-04-01 | 2022-09-21 |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Doug Skilling | owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag1 | Continuous |  | 0.2 GPH |  | No | No |  | Yes | Biennially |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 | 0.1 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | No | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Doug Skilling | owner | 2022-10-24 09:15 | 2022-10-24 16:45 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | UST Removal | 2 | 10032109-002 | Xeres | A Stand-alone Tank | 10000 | 1982-04-01 | 2022-09-21 |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Doug Skilling | owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag1 | Continuous |  | 0.2 GPH |  | No | No |  | Yes | Biennially |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 | 0.1 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Doug Skilling | owner | 2022-10-24 09:15 | 2022-10-24 16:45 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032109 | 21-000-601274 | Salkhi Petroleum Inc. | 90401812 | Tiburon Chevron | 105 Tiburon Boulevard | Mill Valley | 94941 | UST Removal | 1 | 10032109-001 | Xeres | A Stand-alone Tank | 10000 | 1982-04-01 | 2022-09-21 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Doug Skilling | owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag1 | Continuous |  | 0.2 GPH |  | No | No |  | Yes | Biennially |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480 | 0.1 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | Yes | No | Yes | Yes | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Brittney De La Garza | General Manager | Tank Owner/Operator |  | Doug Skilling | owner | 2022-10-24 09:15 | 2022-10-24 16:45 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032112 | 21-000-600064 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron #98933 | 301 Sir Francis Drake Boulevard | Greenbrae | 94904 | Confirmed/Updated Information | 2 | 10032112-002 | XERXES | A Stand-alone Tank | 20000 | 2004-12-01 |  |  | 1 | T2-REGULAR (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE | RETAIL HES | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 330020-464 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 330020-464 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-464 & VR-209 SENSORS. VENT & UDC SUMPS MONITORED BY VR-464 & VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY & OVERFILL ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER) PRIMARY & EXTERNAL ALARM. EVR ISD SOFTWARE. | MANAGER | MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | CHARLES BITTLE | RETAIL HES | 2024-04-29 10:37 | 2024-05-10 10:18 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032112 | 21-000-600064 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron #98933 | 301 Sir Francis Drake Boulevard | Greenbrae | 94904 | Confirmed/Updated Information | 1 | 10032112-001 | XERXES | A Stand-alone Tank | 15000 | 2004-12-01 |  |  | 1 | T1-SUPREME (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE | RETAIL HES | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 330020-464 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 330020-464 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-464 & VR-209 SENSORS. VENT & UDC SUMPS MONITORED BY VR-464 & VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY & OVERFILL ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER) PRIMARY & EXTERNAL ALARM. EVR ISD SOFTWARE. | MANAGER | MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | CHARLES BITTLE | RETAIL HES | 2024-04-29 10:37 | 2024-05-10 10:18 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032118 | 21-000-600067 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 92071 | 22 Rowland Way | Novato | 94945 | Confirmed/Updated Information | 2 | 10032118-002 | JOOR | A Stand-alone Tank | 12000 | 1989-01-01 |  |  | 1 | T2-SUPREME (PER VEEDER-ROOT PROGRAMMING)- DW STEEL CLAD W/FRP | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350R | VEEDER ROOT | 794380-352 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | FILL & UDC SUMPS MONITORED BY VR-208. VAPOR POT MONITORING: VR-208 =SUMP, VR-420 =ANNULAR, VR-420 =HIGH LEVEL & VR-420 =LOW POINT. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD. | MANAGER | MANAGER | ASSISTANT MANAGER | ASSISTANT MANAGER | Tank Owner/Operator |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | 2023-12-22 12:01 | 2024-01-31 13:40 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032118 | 21-000-600067 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 92071 | 22 Rowland Way | Novato | 94945 | Confirmed/Updated Information | 3 | 10032118-003 | JOOR | A Stand-alone Tank | 12000 | 1989-01-01 |  |  | 1 | T3-REGULAR (PER VEEDER-ROOT PROGRAMMING) DW STEEL CLAD W/FRP | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350R | VEEDER ROOT | 794380-208 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP), FILL & UDC SUMPS MONITORED BY VR-208 SENSORS. VAPOR POT MONITORING: VR-208 =SUMP, VR-420 =ANNULAR, VR-420 =HIGH LEVEL & VR-420 =LOW POINT. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD. | MANAGER | MANAGER | ASSISTANT MANAGER | ASSISTANT MANAGER | Tank Owner/Operator |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | 2023-12-22 12:01 | 2024-01-31 13:40 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032118 | 21-000-600067 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | Chevron Station # 92071 | 22 Rowland Way | Novato | 94945 | Confirmed/Updated Information | 1 | 10032118-001 | JOOR | A Stand-alone Tank | 12000 | 1989-01-01 |  |  | 1 | T1-DIESEL (PER VEEDER-ROOT PROGRAMMING) - DW STEEL CLAD W/FRP | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350R | VEEDER ROOT | 794380-352 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350R | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | STP SUMP MONITORED BY VR-352. FILL & UDC SUMPS MONITORED BY VR-208. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). | MANAGER | MANAGER | ASSISTANT MANAGER | ASSISTANT MANAGER | Tank Owner/Operator |  | CLAYTON YOUNG | RETAIL HES SPECIALIST | 2023-12-22 12:01 | 2024-01-31 13:40 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032121 | 21-000-601314 | AS Convenience & Energy Inc. | 90379039 | Strawberry Chevron Gas | 584 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10032121-003 | Modern Welding | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Steel |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | No | Yes | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:12 | 2024-01-08 09:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032121 | 21-000-601314 | AS Convenience & Energy Inc. | 90379039 | Strawberry Chevron Gas | 584 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10032121-001 | Modern Welding | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Steel |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | No | Yes | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:12 | 2024-01-08 09:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032121 | 21-000-601314 | AS Convenience & Energy Inc. | 90379039 | Strawberry Chevron Gas | 584 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10032121-002 | Modern Welding | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Steel |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | No | Yes | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:12 | 2024-01-08 09:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032121 | 21-000-601314 | AS Convenience & Energy Inc. | 90379039 | Strawberry Chevron Gas | 584 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 4 | 10032121-004 | Modern Welding | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Steel |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | No | Yes | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:12 | 2024-01-08 09:46 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032184 | 21-000-601233 | Fara's Auto | 90684112 | Fara's Auto | 98 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 2 | 10032184-002 | Jool | One in a Compartmented Unit | 5000 | 1998-11-01 |  |  | 2 | One tank with two compartments- 1 (9K) Regular, 1 (6K) Supreme. | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  |  | Steel |  | None |  | Single-walled | Steel |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder-Root | TLS 350 | Veeder-Root | VR 420 | Yes | Veeder-Root | TLS 350 | Veeder-Root | VR Mag Probe | Continuous |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS 350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Red Jacket | MLLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  |  | Veeder-Root | 330212-001 | No | No | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nik Zagorov | Eco-Check Compliance | Nick Fara | President |  |  |  |  | 2024-05-20 17:29 | 2024-05-21 10:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032184 | 21-000-601233 | Fara's Auto | 90684112 | Fara's Auto | 98 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 1 | 10032184-001 | Jool | One in a Compartmented Unit | 9000 | 1998-11-01 |  |  | 2 | One tank with two compartments- 1 (9K) Regular, 1 (6K) Supreme. | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  |  | Steel |  | None |  | Single-walled | Steel |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Gary Heller | President | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder-Root | TLS 350 | Veeder-Root | VR 420 | Yes | Veeder-Root | TLS 350 | Veeder-Root | VR Mag Probe | Continuous |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS 350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Red Jacket | MLLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  |  | Veeder Root | 330212-001 | No | No | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nick Zagorov | Eco-Check Compliance | Nick Fara | President | Authorized Representative of Owner |  | Gary Heller | President | 2024-05-20 17:29 | 2024-05-21 10:35 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032214 | 21-000-600112 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Woodlands | 1 Kent Avenue | Kentfield | 94904 | Confirmed/Updated Information | 3 | 10032214-003 | Owens Corning | A Stand-alone Tank | 6000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  |  | Fiberglass |  | Fiberglass |  | None |  | None |  | Yes | No | No | Single-walled | Other |  | No | No | No |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794390-407 | No | [8 empty] | Yes | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | No | Yes |  |  |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | [8 empty] | Yes |  | Nicola Zagorov | Designated Operator | Edy Diaz | Operations Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-01-03 12:33 | 2024-01-11 12:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032214 | 21-000-600112 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Woodlands | 1 Kent Avenue | Kentfield | 94904 | Confirmed/Updated Information | 2 | 10032214-002 | Owens Corning | A Stand-alone Tank | 10000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  |  | Fiberglass |  | Fiberglass |  | None |  | None |  | Yes | No | No | Single-walled | Other |  | No | No | No |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794390-409 | No | [8 empty] | Yes | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | No | Yes |  |  |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | [8 empty] | Yes |  | Nicola Zagorov | Designated Operator | Edy Diaz | Operations Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-01-03 12:33 | 2024-01-11 12:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032214 | 21-000-600112 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Woodlands | 1 Kent Avenue | Kentfield | 94904 | Confirmed/Updated Information | 1 | 10032214-001 | Owens Corning | A Stand-alone Tank | 10000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | None |  | None |  | Yes | No | No | Single-walled | Other |  | No | No | No |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Dry | Veerder Root | TLS 350 | Veeder Root | 794390-407 | No | [8 empty] | Yes | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | No | Yes |  |  |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | No | [8 empty] | Yes |  | Nicola Zagorov | Designated Operator | Edy Diaz | Operations Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2024-01-03 12:33 | 2024-01-11 12:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032220 | 21-000-601224 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Miller Avenue | 458 Miller Avenue | Mill Valley | 94941 | Renewal Permit | 1 | 10032220-001 | Joor Manufacturing | One in a Compartmented Unit | 8000 | 1993-07-01 |  |  | 4 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Steel |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Steel |  | Yes | Yes | Yes | Double-walled | Steel |  | No | No | No |  | Albert Uong | UST Operator | Annually |  | Site Plan Previously Submitted | Yes | Dry | INCON | INCON | INCON |  | Yes | INCON | TS-5000 | INCON | INCON | Continuous |  | 0.2 GPH |  | No | No |  | Yes | Annually |  | No |  | No | [7 empty] | Yes | VAPORLESS | 99 LD 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly |  | Bravo |  |  | DISP 7/8 VR 330212-001 | No | Yes | Yes | Yes | Single-walled |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Nik Zagorov | Designated Operator |  |  | Tank Owner/Operator |  | Albert Uong | UST Operator | 2024-01-03 09:45 | 2024-01-10 02:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032220 | 21-000-601224 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Miller Avenue | 458 Miller Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10032220-003 | Joor Manufacturing | One in a Compartmented Unit | 4000 | 1993-07-01 |  |  | 4 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Steel |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Double-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Albert Uong; UST Tank Certification / Applicant Information 472: UST Operator; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: INCON; Continuous Electronic Tank Monitoring 490-8: INCON; Continuous Electronic Tank Monitoring 490-9: INCON; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: INCON; Automatic Tank Gauging 490-13: TS-5000; Automatic Tank Gauging 490-14: INCON; Automatic Tank Gauging 490-15: INCON; Automatic Tank Gauging 490-16: Continuous; Automatic Tank Gauging 490-18: 0.2 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-55: Bravo; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: Yes; Under Dispenser Containment (UDC) Monitoring 490-61: Yes; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Nik Zagorov; Personnel Responsibilities 490-73: Designated Operator; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Albert Uong; UST Monitoring Plan Certification / Applicant Information 490-79: UST Operator | 2024-01-03 09:45 | 2024-01-10 02:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032220 | 21-000-601224 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Miller Avenue | 458 Miller Avenue | Mill Valley | 94941 | UST Removal | 8742 | 10032220-005 | Joor Manufacturing | One in a Compartmented Unit | 20000 | 1993-10-31 | 1899-12-31 |  | 4 | This facility has a UST with 4 compartments. This UST #8742 was submitted as one tank with 4 compartments, I am submitting it as permanently closed/UST removal to delete it, and the 4 systems have already been submitted individually as Tank #1, 2, 3, & 4. | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Steel |  | Fiberglass |  | Double-walled | Steel |  | Fiberglass |  | Double-walled | Steel |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | No |  | Albert Uong | UST Operator | Annually |  | Site Plan Previously Submitted | Yes | Dry | INCON | TS-5000 | INCON | TSP-ULS | Yes | INCON | TS-5000 | INCON | TSP-ULS | Continuous |  | 0.2 GPH |  | No | No |  | Yes | Annually |  | No |  | Yes | Dry | INCON | TS-5000 | INCON | TLS-ULS |  | Yes | No |  |  | Yes | INCON | TLS-ULS | 0.2 GPH | Yes | Yes | Yes | Every 3 Years |  | No |  | No | No | No |  | Continuous |  | INCON | TS-5000 | INCON | TSP-ULS | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | Yes | Yes | Yes | Yes | Yes | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Albert Uong | Designate UST Operator |  |  | Authorized Representative of Owner |  | Albert Uong | UST Operator | 2017-08-25 08:03 | 2017-08-25 08:34 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032220 | 21-000-601224 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Miller Avenue | 458 Miller Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 4 | 10032220-004 | Joor Manufacturing | One in a Compartmented Unit | 4000 | 1993-07-01 |  |  | 4 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Steel |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Double-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Albert Uong; UST Tank Certification / Applicant Information 472: UST Operator; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: INCON; Continuous Electronic Tank Monitoring 490-8: INCON; Continuous Electronic Tank Monitoring 490-9: INCON; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: INCON; Automatic Tank Gauging 490-13: TS-5000; Automatic Tank Gauging 490-14: INCON; Automatic Tank Gauging 490-15: INCON; Automatic Tank Gauging 490-16: Continuous; Automatic Tank Gauging 490-18: 0.2 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-55: Bravo; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: Yes; Under Dispenser Containment (UDC) Monitoring 490-61: Yes; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Nik Zagorov; Personnel Responsibilities 490-73: Designated Operator; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Albert Uong; UST Monitoring Plan Certification / Applicant Information 490-79: UST Operator | 2024-01-03 09:45 | 2024-01-10 02:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032220 | 21-000-601224 | DS Petroleum LLC | 90833503 | Fuel 24:7 @ Miller Avenue | 458 Miller Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10032220-002 | Joor Manufacturing | One in a Compartmented Unit | 4000 | 1993-07-01 |  |  | 4 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Steel |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Double-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Albert Uong; UST Tank Certification / Applicant Information 472: UST Operator; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: INCON; Continuous Electronic Tank Monitoring 490-8: TS-5000; Continuous Electronic Tank Monitoring 490-9: INCON; Continuous Electronic Tank Monitoring 490-10: TS-ULS; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: INCON; Automatic Tank Gauging 490-13: TS-5000; Automatic Tank Gauging 490-14: INCON; Automatic Tank Gauging 490-15: TS-LL2-113; Automatic Tank Gauging 490-16: Continuous; Automatic Tank Gauging 490-18: 0.2 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-55: Bravo; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: Yes; Under Dispenser Containment (UDC) Monitoring 490-61: Yes; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Nik Zagorov; Personnel Responsibilities 490-73: Designated Operator; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Albert Uong; UST Monitoring Plan Certification / Applicant Information 490-79: UST Operator | 2024-01-03 09:45 | 2024-01-10 02:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032229 | 21-000-600118 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 801 Golden Gate Place | Novato | 94947 | Confirmed/Updated Information | 1 | 10032229-002 | Joor Mfr. | A Stand-alone Tank | 15000 | 1998-04-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Other |  | Flexible |  | Single-walled | Other |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Karen Shelar; UST Tank Certification / Applicant Information 472: EH&S Specialist; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: 350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: No; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-69i: SPCC; Training 490-70: No; Personnel Responsibilities 490-72: Bill Stafford; Personnel Responsibilities 490-73: Director of Risk Management; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Karen Shelar; UST Monitoring Plan Certification / Applicant Information 490-79: EH&S Specialist | 2023-06-12 17:38 | 2023-11-09 13:56 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032229 | 21-000-600118 | Golden Gate Bridge Highway and Transportation District | 90077089 | Golden Gate Transit | 801 Golden Gate Place | Novato | 94947 | Confirmed/Updated Information | 2 | 10032229-001 | Joor Mfr. | A Stand-alone Tank | 15000 | 1998-04-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Other |  | Flexible |  | Single-walled | Other |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Karen Shelar; UST Tank Certification / Applicant Information 472: EH&S Specialist; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: 350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: No; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-69i: SPCC; Training 490-70: No; Personnel Responsibilities 490-72: Bill Stafford; Personnel Responsibilities 490-73: Director of Risk Management; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Karen Shelar; UST Monitoring Plan Certification / Applicant Information 490-79: EH&S Specialist | 2023-06-12 17:38 | 2023-11-09 13:56 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032250 | 21-000-601334 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 382136/2224 | 2070 REDWOOD HIGHWAY | LARKSPUR | 94939 | Confirmed/Updated Information | 2 | 10032250-002 | MODERN WELDING | A Stand-alone Tank | 10000 | 1993-01-01 |  |  | 1 | T2-REGULAR (PER VEEDER-ROOT PROGRAMMING) - THIS TANK IS MANIFOLDED TO TANK 3. YEAR OF INSTALLATION IS 1993. EXACT DATE IS UNKNOWN | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | VIC SOSSIKIAN | OWNER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) SUMP MONITORED BY VR-209 SENSOR. UDC SUMPS MONITORED BY VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | VIC SOSSIKIAN | OWNER | 2024-04-29 13:45 | 2024-05-10 10:34 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032250 | 21-000-601334 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 382136/2224 | 2070 REDWOOD HIGHWAY | LARKSPUR | 94939 | Confirmed/Updated Information | 4 | 10032250-004 | MODERN WELDING | A Stand-alone Tank | 10000 | 1993-01-01 |  |  | 1 | T1-SUPREME (PER VEEDER-ROOT PROGRAMMING) - YEAR OF INSTALLATION IS 1993. EXACT DATE IS UNKNOWN | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | VIC SOSSIKIAN | OWNER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) SUMP MONITORED BY VR-209 SENSOR. UDC SUMPS MONITORED BY VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | VIC SOSSIKIAN | OWNER | 2024-04-29 13:45 | 2024-05-10 10:34 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032250 | 21-000-601334 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 382136/2224 | 2070 REDWOOD HIGHWAY | LARKSPUR | 94939 | Confirmed/Updated Information | 1 | 10032250-001 | MODERN WELDING | A Stand-alone Tank | 10000 | 1993-01-01 |  |  | 1 | T4-DIESEL (PER VEEDER-ROOT PROGRAMMING) - INSTALLATION DATE IN YEAR 1993. EXACT DATE IS UNKNOWN. | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | VIC SOSSIKIAN | OWNER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & ACCESS SUMPS MONITORED BY VR-209 SENSORS. UDC SUMPS MONITORED BY VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | VIC SOSSIKIAN | OWNER | 2024-04-29 13:45 | 2024-05-10 10:34 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032250 | 21-000-601334 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 382136/2224 | 2070 REDWOOD HIGHWAY | LARKSPUR | 94939 | Renewal Permit | 3 | 10032250-003 | MODERN WELDING | A Stand-alone Tank | 10000 | 1993-01-01 |  |  | 1 | T3-REGULAR (PER VEEDER-ROOT PROGRAMMING) - THIS TANK IS THE MANIFOLDED WITH TANK 2. IT IS THE MASTER TANK. YEAR OF INSTALLATION IS 1993. EXACT DATE OF INSTALLATION IS UNKNOWN | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | VIC SOSSIKIAN | OWNER | Annually |  | New Plan Submitted | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 | VEEDER-ROOT | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) SUMP MONITORED BY VR-209 SENSOR. UDC SUMPS MONITORED BY VR-208 SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD SOFTWARE INSTALLED. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | VIC SOSSIKIAN | OWNER | 2024-04-29 13:45 | 2024-05-10 10:34 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032280 | 21-000-601335 | Rino Fairfax Service | 90763432 | Rino Fairfax Service | 1942 Sir Francis Drake Boulevard | Fairfax | 94930 | Confirmed/Updated Information | 87-B | 10032280-003 | Modern Welding | A Stand-alone Tank | 10000 | 1999-07-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Steel |  | Yes | No | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Georgina Sandino | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/352 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Miguel Vargas | Operator | Maria Romero | Operator | Tank Owner/Operator |  | Georgina Sandino | Owner | 2023-09-05 10:32 | 2023-09-05 12:51 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032280 | 21-000-601335 | Rino Fairfax Service | 90763432 | Rino Fairfax Service | 1942 Sir Francis Drake Boulevard | Fairfax | 94930 | Renewal Permit | 87-A | 10032280-001 | Modern Welding | A Stand-alone Tank | 10000 | 1999-07-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Steel |  | Yes | No | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Georgina Sandino | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/352 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Miguel Vargas | Operator | Maria Romero | Operator | Tank Owner/Operator |  | Georgina Sandino | Owner | 2023-09-05 10:32 | 2023-09-05 12:51 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032280 | 21-000-601335 | Rino Fairfax Service | 90763432 | Rino Fairfax Service | 1942 Sir Francis Drake Boulevard | Fairfax | 94930 | Renewal Permit | 91 | 10032280-002 | Modern Welding | A Stand-alone Tank | 10000 | 1999-07-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Steel |  | Yes | No | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Georgina Sandino | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/352 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Miguel Vargas | Operator | Maria Romero | Operator | Tank Owner/Operator |  | Georgina Sandino | Owner | 2023-09-05 10:32 | 2023-09-05 12:51 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032328 | 21-000-600160 | Chevron Station # 91014 | 90621880 | RAJA CROMWELL, INC. | 1549 South Novato Boulevard | Novato | 94947 | Confirmed/Updated Information | 3 | 10032328-003 | Xerxes | A Stand-alone Tank | 11527 | 1997-09-09 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | None |  |  |  | None | None |  |  |  | Steel |  |  |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root 350 | Veeder Root | Veeder Root 409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | 350 | Veeder Root | 352 |  | Yes | No |  |  | Yes | Veeder Root | PLLD | 0.1 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | 350 | VR | 208 | Yes | Yes | Yes | Yes | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Dilek Tulca | Owner | [6 empty] | 2023-01-11 12:14 | 2023-01-11 12:58 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032328 | 21-000-600160 | Chevron Station # 91014 | 90621880 | RAJA CROMWELL, INC. | 1549 South Novato Boulevard | Novato | 94947 | Confirmed/Updated Information | 1 | 10032328-001 | Xerxes | A Stand-alone Tank | 11527 | 1997-09-10 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled |  |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root 350 | Veeder Root | Veeder Root 409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | 350 | Veeder Root | 352 |  | Yes | No |  |  | Yes | Veeder Root | PLLD | 0.1 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | 350 | VR | 208 | Yes | Yes | Yes | Yes | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Dilek Tulca | Owner | [6 empty] | 2023-01-11 12:14 | 2023-01-11 12:58 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032328 | 21-000-600160 | Chevron Station # 91014 | 90621880 | RAJA CROMWELL, INC. | 1549 South Novato Boulevard | Novato | 94947 | Confirmed/Updated Information | 2 | 10032328-002 | Xerxes | A Stand-alone Tank | 11527 | 1997-09-09 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root 350 | Veeder Root | Veeder Root 409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | 350 | Veeder Root | 352 |  | Yes | No |  |  | Yes | Veeder Root | PLLD | 0.1 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | 350 | VR | 208 | Yes | Yes | Yes | Yes | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Dilek Tulca | Owner | [6 empty] | 2023-01-11 12:14 | 2023-01-11 12:58 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032337 | 21-000-601283 | Redwood Oil Company, Inc. | 90370903 | Point Reyes Station | 11401 State Route 1 | Pt. Reyes | 94956 | UST Removal | M588102 | 10032337-003 | Trusco | One in a Compartmented Unit | 4000 | 1998-10-21 | 2017-07-21 |  | 2 | This is a duplicate Tank ID#. Both Diesel and Premium Unleaded have the same Tank ID#, therefore, CERS is reading two tanks instead of three. Deleted this tank with today's date as the UST closure date, and will be creating a new tank ID# for the Premium Unleaded (M588102). (Nadira Alicusic, Marin County CUPA). | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Jacketed |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Other |  | No | No | Yes |  | Mark Reano | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350R | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes |  | Veeder Root | TLS 350R | Veeder Root | 208 | Yes | Yes | Yes | Vaporless | MLLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | [8 empty] | Yes |  | Mark Reano | owner | John Plumeri | manager | Facility Owner/Operator |  | Mark Reano | owner | 2021-01-28 07:11 | 2021-01-28 08:14 | Tracey Nguyen | Marin County Dept of Public Works CUPA | CUPA
10032337 | 21-000-601283 | Redwood Oil Company, Inc. | 90370903 | Point Reyes Station | 11401 State Route 1 | Pt. Reyes | 94956 | Confirmed/Updated Information | M588101 | 10032337-002 | Trusco | One in a Compartmented Unit | 8000 | 1998-10-21 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Jacketed |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Other |  | No | No | Yes |  | Mark Reano | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350R | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes |  | Veeder Root | TLS 350R | Veeder Root | 208 | Yes | Yes | Yes | Vaporless | MLLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | [8 empty] | Yes |  | Mark Reano | owner | John Plumeri | manager | Facility Owner/Operator |  | Mark Reano | owner | 2023-02-07 11:06 | 2023-11-09 13:50 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032337 | 21-000-601283 | Redwood Oil Company, Inc. | 90370903 | Point Reyes Station | 11401 State Route 1 | Pt. Reyes | 94956 | Confirmed/Updated Information | M588102 | 10032337-004 | Trusco | One in a Compartmented Unit | 4000 | 1998-10-21 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Jacketed |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Other; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: TLS 350R; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS 350R; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Fe Petro; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: MLLD; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: No; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: No; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Mark Reano; Personnel Responsibilities 490-73: owner; Personnel Responsibilities 490-74: John Plumeri; Personnel Responsibilities 490-75: manager; UST Monitoring Plan Certification / Applicant Information 490-76: Facility Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Mark Reano; UST Monitoring Plan Certification / Applicant Information 490-79: owner | 2023-02-07 11:06 | 2023-11-09 13:50 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032337 | 21-000-601283 | Redwood Oil Company, Inc. | 90370903 | Point Reyes Station | 11401 State Route 1 | Pt. Reyes | 94956 | Confirmed/Updated Information | M588114 | 10032337-001 | Trusco | A Stand-alone Tank | 12000 | 1998-10-21 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Jacketed |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Other |  | No | No | Yes |  | Mark Reano | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350R | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes |  | Veeder Root | TLS 350R | Veeder Root | 208 | Yes | Yes | Yes | Fe Petro | MLLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | [8 empty] | Yes |  | Mark Reano | owner | John Plumeri | manager | Facility Owner/Operator |  | Mark Reano | owner | 2023-02-07 11:06 | 2023-11-09 13:50 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032343 | 21-000-600167 | Marin Municipal Water District | 90097819 | Marin Municipal Water District - Corporation Yard | 220 Tamal Vista Boulevard | Corte Madera | 94925 | Renewal Permit | 1 | 10032343-001 | Modern Welding | A Stand-alone Tank | 10000 | 1985-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | No | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | David Peery | Safety and Risk Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 0794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 0794380-208 | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 0794380-208 | Yes | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Darren Machado | Director of Operations | Mark Hedeen | Superintendent of Systems Maintenance | Authorized Representative of Owner |  | David Peery | Safety and Risk Manager | 2024-06-05 14:00 | 2024-06-06 12:41 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032364 | 21-000-600177 | Marin General Hospital | 90103375 | MarinHealth Medical Center | 250 Bon Air Road | Greenbrae | 94904 | Confirmed/Updated Information | FOT-2 | 10032364-002 | Xerxes | A Stand-alone Tank | 35000 | 2019-07-02 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | None |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Liquid-Filled; Continuous Electronic Tank Monitoring 490-7: Franklin; Continuous Electronic Tank Monitoring 490-8: TS550EVO; Continuous Electronic Tank Monitoring 490-9: Franklin; Continuous Electronic Tank Monitoring 490-10: TSP-ULS; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Under Vacuum; Continuous Monitoring of Piping Secondary Containment 490-30: Franklin; Continuous Monitoring of Piping Secondary Containment 490-31: TS550EVO; Continuous Monitoring of Piping Secondary Containment 490-32: Franklin; Continuous Monitoring of Piping Secondary Containment 490-33: TSP-ULS; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Darren Nakatani; Personnel Responsibilities 490-73: Chief Engineer; Personnel Responsibilities 490-74: Damon George; Personnel Responsibilities 490-75: Director, Facilities & Engineering | 2024-03-15 17:18 | 2024-04-19 11:59 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032364 | 21-000-600177 | Marin General Hospital | 90103375 | MarinHealth Medical Center | 250 Bon Air Road | Greenbrae | 94904 | Renewal Permit | 1 | 10032364-001 | XERXES | A Stand-alone Tank | 10000 | 1989-06-01 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | None | Steel |  | None |  | None | None |  | None |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Darren Nakatani; UST Tank Certification / Applicant Information 472: Cheif Engineer; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Liquid-Filled; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794380-301; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: No; Personnel Responsibilities 490-72: Darren Nakatani; Personnel Responsibilities 490-73: Cheif Engineer; Personnel Responsibilities 490-74: Shawn Mann; Personnel Responsibilities 490-75: Asst Cheif Engineer; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Darren Nakatani; UST Monitoring Plan Certification / Applicant Information 490-79: Cheif Engineer | 2024-03-15 17:18 | 2024-04-19 11:59 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032370 | 21-000-600179 | County of Marin | 90404194 | County of Marin/Civic Center Jail | 13 Peter Behr Drive | San Rafael | 94903 | Confirmed/Updated Information | Jail 1 | 10032370-001 | Owens Corning | A Stand-alone Tank | 4000 | 1994-01-03 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | Yes | No | No | Double-walled | Pressure | Unknown |  | Unknown |  | Single-walled | Steel | [12 empty] | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Eric Steger; UST Tank Certification / Applicant Information 472: Assistant Director of Public Works; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Liquid-Filled; Continuous Electronic Tank Monitoring 490-7: INCON; Continuous Electronic Tank Monitoring 490-8: TS- 550EVO; Continuous Electronic Tank Monitoring 490-9: INCON; Continuous Electronic Tank Monitoring 490-10: TSP-HIS; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Pressurized; Continuous Monitoring of Piping Secondary Containment 490-30: INCON; Continuous Monitoring of Piping Secondary Containment 490-31: TS-550EVO; Continuous Monitoring of Piping Secondary Containment 490-32: INCON; Continuous Monitoring of Piping Secondary Containment 490-33: TSP-ULS; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Todd Pressley; Personnel Responsibilities 490-73: Building & Maintenance manager; Personnel Responsibilities 490-74: Tom Harp; Personnel Responsibilities 490-75: Building Maintenance Supervisor; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Dean Joyner; UST Monitoring Plan Certification / Applicant Information 490-79: Env Comp Spec | 2023-12-21 08:28 | 2024-07-17 13:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032391 | 21-000-600187 | Tamalpais Community Services District | 90103477 | Tamalpais Community Services District | 305 Bell Lane | Mill Valley | 94941 | Renewal Permit | 2 | 10032391-002 | Joor | One in a Compartmented Unit | 500 | 1995-03-01 |  |  | 2 | 1,000 gal diesel and 500 gal gas | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Double-walled | 23 CCR §2636(a)(3) Suction | Flexible |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | No |  | Robert Bunce | Public Works Superintendent | Annually |  | Site Plan Previously Submitted | Yes | Dry | Franklin Fueling | TS-550 EVO | Franklin Fueling | TSP-ULS | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Franklin Fueling | TS-550 EVO | Franklin Fueling | TSP-ULS | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | Franklin Fueling | TS-550 EVO | Franklin Fueling | TSP-ULS | Yes | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Mike Quecke | Public Works Superintendent | Kristopher Florid | Maintenance | Facility Owner/Operator |  | Robert Bunce | Public Works Superintendent | 2023-11-06 13:43 | 2023-11-06 14:47 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032391 | 21-000-600187 | Tamalpais Community Services District | 90103477 | Tamalpais Community Services District | 305 Bell Lane | Mill Valley | 94941 | Renewal Permit | 1 | 10032391-001 | Joor | One in a Compartmented Unit | 1000 | 1995-03-01 |  |  | 2 | 1,000 gal diesel and 500 gal gas | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Double-walled | 23 CCR §2636(a)(3) Suction | Flexible |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | No |  | Robert Bunce | Public Works Superintendent | Annually |  | Site Plan Previously Submitted | Yes | Dry | Franklin Fueling | TS-550 EVO | Franklin Fueling | TSP-ULS | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Franklin Fueling | TS-550 EVO | Franklin Fueling | TSP-ULS | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | Franklin Fueling | TS-550 EVO | Franklin Fueling | TSP-ULS | Yes | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Mike Quecke | Public Works Superintendent | Kristopher Florid | Maintenance | Facility Owner/Operator |  | Robert Bunce | Public Works Superintendent | 2023-11-06 13:43 | 2023-11-06 14:47 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032436 | 21-000-600203 | Boyett Petroleum | 90144817 | Corte Madera Kwik Serv - BW # 110 | 516 Tamalpais Drive | Corte Madera | 94925 | Renewal Permit | 2 | 10032436-002 | UNKNOWN | A Stand-alone Tank | 12000 | 1996-07-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: B & W PETROLEUM c/o Monica Farhat; UST Tank Certification / Applicant Information 472: CUSTOMER SERVICE COORDINATOR; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: FE PETRO; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: STP-MLD; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: No; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: OLD STATION SERVICE/MARK FAJARDIN; Personnel Responsibilities 490-73: TESTING COMPANY; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: B & W PETROLEUM c/o Monica Farhat; UST Monitoring Plan Certification / Applicant Information 490-79: CUSTOMER SERVICE COORDINATOR | 2024-03-04 09:24 | 2024-08-01 10:59 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032436 | 21-000-600203 | Boyett Petroleum | 90144817 | Corte Madera Kwik Serv - BW # 110 | 516 Tamalpais Drive | Corte Madera | 94925 | Renewal Permit | 1 | 10032436-001 | OWENS CORNING | A Stand-alone Tank | 12000 | 1996-07-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | No | No | No |  | B & W PETROLEUM c/o Monica Farhat | CUSTOMER SERVICE COORDINATOR | Annually |  | Site Plan Previously Submitted | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS-350 | VEEDER ROOT | 208 | Yes | Yes | Yes | FE PETRO | STP-MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Rick Jewel | Maintenance Manager | Monica Farhat | Compliance Coordinator | Authorized Representative of Owner |  | B & W PETROLEUM c/o Monica Farhat | CUSTOMER SERVICE COORDINATOR | 2024-03-04 09:24 | 2024-08-01 10:59 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032448 | 21-000-600207 | City of Novato Police Department | 90103690 | City of Novato Police Department | 909 Machin Avenue | Novato | 94945 | Confirmed/Updated Information | 2 | 10032448-002 | Owens/ Corning | A Stand-alone Tank | 1000 | 1979-03-01 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | Yes | No Dispensers | None |  | No | No | Yes |  | Mike Brunelle | Equipment Supervisor | Annually |  | Site Plan Previously Submitted | Yes | [5 empty] | Yes | Gilbarco | TSL 300C | Tristate Single Float | MAG 7 | Daily/Nightly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | GILBARCO | TSL-300C | Gilbarco/ VeederRoot | 394390-208 | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | No Dispensers |  |  |  | Veeder Root | 394390-208 | No | No | No | No | Single-walled | Liquid | No | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Mike Brunelle | Equipment Supervisor | Lyle Waite | Maintenance Superintendant | Authorized Representative of Owner |  | Mike Brunelle | Equipment Supervisor | 2023-12-19 14:43 | 2023-12-19 15:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032448 | 21-000-600207 | City of Novato Police Department | 90103690 | City of Novato Police Department | 909 Machin Avenue | Novato | 94945 | Confirmed/Updated Information | 1 | 10032448-001 | Owens-Corning | A Stand-alone Tank | 10000 | 1974-06-25 |  |  | 1 | Phase 1 suction system | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Single-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | None |  | None | Fiberglass |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Mike Brunelle; UST Tank Certification / Applicant Information 472: Equipment Supervisor; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: Gilbarco; Automatic Tank Gauging 490-13: PAO0292011002B; Automatic Tank Gauging 490-14: Tri State; Automatic Tank Gauging 490-15: Single Float-MAG 7; Automatic Tank Gauging 490-16: Daily/Nightly; Automatic Tank Gauging 490-18: 0.2 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Continuous; Under Dispenser Containment (UDC) Monitoring 490-57: Veeder-Root; Under Dispenser Containment (UDC) Monitoring 490-58: 847990-001; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: Yes; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Mike Brunelle; Personnel Responsibilities 490-73: Equipment Supervisor; Personnel Responsibilities 490-74: Lyle Waite; Personnel Responsibilities 490-75: Maintenance Superintendant; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Mike Brunelle; UST Monitoring Plan Certification / Applicant Information 490-79: Equipment Supervisor | 2023-12-19 14:43 | 2023-12-19 15:15 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032457 | 21-000-600211 | Marin Municipal Water District | 90097819 | Marin Municipal Water District - Ranger Station | 49 Sky Oaks Rd | Fairfax | 94930 | Renewal Permit | 1 | 10032457-001 | Trusco | A Stand-alone Tank | 2000 | 1991-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Jacketed |  | Yes | No | Yes | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Double-walled | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | David Peery | Safety and Risk Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | No | No | No |  |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Crystal Yezman | Facilities & Watershed Division Manager | Carl Sanders | Maintenance Supervisor | Authorized Representative of Owner |  | David Peery | Safety and Risk Manager | 2022-04-26 12:31 | 2022-10-21 10:23 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032481 | 21-000-600219 | Kentfield and San Francisco Specialty Hospital, Inc. | 90863794 | Kentfield Rehabilitation/Specialty Hospital | 1125 Sir Francis Drake Boulevard | Kentfield | 94904 | Confirmed/Updated Information | 21000010072000001 | 10032481-001 | Owens-Corning | A Stand-alone Tank | 500 | 1985-10-01 |  | 1985-10-01 | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | No | No | Double-walled | Conventional Suction | Rigid Plastic |  | Rigid Plastic |  |  | Steel |  | Steel |  | Double-walled | Fiberglass |  |  |  | Fiberglass |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Tito B Galvez; UST Tank Certification / Applicant Information 472: Director of Plant Operations; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-302; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: No; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: No; Under Dispenser Containment (UDC) Monitoring 490-64a: Pressure; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Jhon Lantican; Personnel Responsibilities 490-73: Director of Plant Operations; Personnel Responsibilities 490-74: Antonio Mira; Personnel Responsibilities 490-75: Engineer; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Tito B Galvez; UST Monitoring Plan Certification / Applicant Information 490-79: Director of Plant Operations | 2019-02-25 12:20 | 2019-05-30 12:51 | Mary Skramstad | Marin County Dept of Public Works CUPA | CUPA
10032493 | 21-000-600223 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - W3176 | 101 Kleinert Way | Tiburon | 94920 | Confirmed/Updated Information | W3176U001 | 10032493-001 | Modern Welding | A Stand-alone Tank | 2000 | 1987-01-01 |  |  | 1 | UST is located southeast of building exterior in an ungated area of the property. | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Other |  | Yes | No | No | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Sarah Bullock; UST Tank Certification / Applicant Information 472: Authorized Agent to AT&T; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: (L1)Annular Space - 794390-420;(L2)Piping Sump, (L3) Generator Pan Sensor - 794380-208.; Personnel Responsibilities 490-72: Tait Environmental Services; Personnel Responsibilities 490-73: AT&T Authorized Vendor; Personnel Responsibilities 490-74: AT&T Environmental Health and Safety; Personnel Responsibilities 490-75: Call Center; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Sarah Bullock; UST Monitoring Plan Certification / Applicant Information 490-79: Authorized Agent to AT&T | 2024-05-31 07:00 | 2024-08-07 13:31 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032499 | 21-000-600225 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - W3006 | 7 King Street | Larkspur | 94939 | Confirmed/Updated Information | W3006U001 | 10032499-001 | Joor | A Stand-alone Tank | 4000 | 1988-01-01 |  |  | 1 | South Side of Building Exterior, Parking Lot | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Other |  | Yes | No | No | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Sarah Bullock; UST Tank Certification / Applicant Information 472: Authorized Agent to AT&T; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-350 Plus; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350 Plus; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: (L1)Annular Space 794390-420;(L2)Fill Sump,(L3) Transition Sump 794380-208.; Personnel Responsibilities 490-72: Tait Environmental Services; Personnel Responsibilities 490-73: AT&T Authorized Vendor; Personnel Responsibilities 490-74: AT&T Environmental Health and Safety; Personnel Responsibilities 490-75: Call Center; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Sarah Bullock; UST Monitoring Plan Certification / Applicant Information 490-79: Authorized Agent to AT&T | 2024-05-31 06:55 | 2024-06-05 14:32 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032502 | 21-000-600226 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - W3012 | 300 E Blithedale Ave | Mill Valley | 94941 | Confirmed/Updated Information | W3012U001 | 10032502-001 | Modern Welding | A Stand-alone Tank | 5000 | 2004-05-01 |  |  | 1 | Tank is located South Of Building Exterior, Parking Lot | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Other |  | Yes | No | No | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Steel |  | Fiberglass |  | Single-walled | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Sarah Bullock; UST Tank Certification / Applicant Information 472: Authorized Agent to AT&T; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-350 Plus; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350 Plus; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-69i: UST Monitoring Plan, Operating Manuals; Training 490-70: Yes; Comments and Additional Information 490-71: (L1)Annular Space 794390-420;(L2)Fill Sump,(L3)Piping Sump,(L4) Transition Sump,(L5)Generator Floor,(L6)Vent Trans Sump 794380-208. Please see UST Monitoring Site Plan for other sensors monitoring tank system.; Personnel Responsibilities 490-72: Tait Environmental Services; Personnel Responsibilities 490-73: AT&T Authorized Vendor; Personnel Responsibilities 490-74: AT&T Environment Health & Safety; Personnel Responsibilities 490-75: Call Center; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Sarah Bullock; UST Monitoring Plan Certification / Applicant Information 490-79: Authorized Agent to AT&T | 2024-05-31 06:57 | 2024-05-31 08:57 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032505 | 21-000-600227 | PACIFIC BELL TELEPHONE COMPANY dba AT&T CALIFORNIA | 90002299 | AT&T California - WC135 | 350 Alameda Del Prado | Novato | 94949 | Confirmed/Updated Information | WC135U001 | 10032505-001 | Modern Welding | A Stand-alone Tank | 4000 | 2004-06-01 |  |  | 1 | The UST is located on the southeast side of the building exterior, near a parking lot in a secured gated property covered in concrete. | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Other |  | Yes | No | No | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Sarah Bullock; UST Tank Certification / Applicant Information 472: Authorized Agent to AT&T; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-350 Plus; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 794390-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350 Plus; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: (L1)Annular Space - 794390-420; (L2)Fill Sump, (L3)Piping Sump,(L4)Transition Sump, (L5)Generator Pan 1,(L6)Generator Pan 2- 794380-208.; Personnel Responsibilities 490-72: Tait Environmental Services; Personnel Responsibilities 490-73: AT&T Authorized Vendor; Personnel Responsibilities 490-74: AT&T Environment Health & Safety; Personnel Responsibilities 490-75: Call Center; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Sarah Bullock; UST Monitoring Plan Certification / Applicant Information 490-79: Authorized Agent to AT&T | 2024-05-31 07:02 | 2024-06-05 14:38 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032508 | 21-000-600228 | Novato Unified School District | 90103927 | NUSD Transportation Yard | 819 Olive Avenue | Novato | 94945 | Confirmed/Updated Information | 2 | 10032508-002 | Xerxes | One in a Compartmented Unit | 3000 | 2006-09-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Mark Silva | Director of MOT | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TlS 350 plus | Veeder Root | 304 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Liquid | Veeder Root | TlS 350 plus | Veeder Root | 208,303 | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | Veeder Root | TlS 350 plus | Veeder Root | 208,303 | Yes | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Mark Silva | Director of MOT | Dave Ashe | Project Manager | Facility Owner/Operator |  | Mark Silva | Director MOT | 2023-06-06 12:11 | 2023-11-09 13:52 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032508 | 21-000-600228 | Novato Unified School District | 90103927 | NUSD Transportation Yard | 819 Olive Avenue | Novato | 94945 | Confirmed/Updated Information | 1 | 10032508-001 | Xerxes | One in a Compartmented Unit | 3000 | 2006-09-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Mark Silva | Director of MOT | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TlS 350 plus | Veeder Root | 304 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Liquid | Veeder Root | TlS 350 plus | Veeder Root | 208,303 | No | No | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | Veeder Root | TlS 350 plus | Veeder Root | 208, 303 | Yes | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Mark Silva | Director of MOT | Dave Ashe | Project Manager | Facility Owner/Operator |  | Mark Silva | Director MOT | 2023-06-06 12:11 | 2023-11-09 13:52 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032514 | 21-000-600231 | Sausalito-Marin City Sanitary District | 90103957 | Sausalito-Marin City Sanitary District - Treatment Plant | 1 East Road | Sausalito | 94965 | UST Permanent Closure on Site | 1 | 10032514-001 | Owens Corning | A Stand-alone Tank | 1000 | 1986-10-01 | 2018-05-31 |  | 1 | tank removed on 5/31/2018 | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | No | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | None | None |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Omar Arias; UST Tank Certification / Applicant Information 472: Operations Superintendent; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Liquid-Filled; Continuous Electronic Tank Monitoring 490-7: Ronan; Continuous Electronic Tank Monitoring 490-8: X76-AST-4X-1; Continuous Electronic Tank Monitoring 490-9: Ronan; Continuous Electronic Tank Monitoring 490-10: LS-3; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Ronan; Continuous Monitoring of Piping Secondary Containment 490-31: X76-AST-4X-1; Continuous Monitoring of Piping Secondary Containment 490-32: Ronan; Continuous Monitoring of Piping Secondary Containment 490-33: LS-3; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Jeff Kingston; Personnel Responsibilities 490-73: General Manager; Personnel Responsibilities 490-74: Omar Arias; Personnel Responsibilities 490-75: Operations Superintendent; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Jeff Kingston; UST Monitoring Plan Certification / Applicant Information 490-79: General Manager | 2018-11-26 07:25 | 2018-11-26 10:35 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032520 | 21-000-600233 | Sausalito-Marin City Sanitary District | 90103957 | Sausalito-Marin City Sanitary District - Main Street PS | 1 Main Street | Sausalito | 94965 | UST Removal | 1 | 10032520-001 | Seamen Corporation | A Stand-alone Tank | 4000 | 1999-10-25 | 2022-08-30 |  | 1 | Liner and bladder removed on 8/23/2022. Tank filled with concrete on 8/30/2022. Soil testing results confirmed negative. | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Internal Bladder |  | Fiberglass |  | Yes | No | No | No | Single-walled | Conventional Suction | Flexible |  | None |  | None | None |  | None |  | None | None |  | None |  | None |  | None |  | Yes | No | No | No Dispensers | None |  | No | No | No |  | Jeff Kingston | General Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | INCON | TS1001 | INCON | TSP-EIS | Yes | PNEUMERCATOR | PNEUMERCATOR | LDE-740 | LS600 | Continuous |  | Other |  | No | No |  | No |  |  | No |  | Yes | Dry | INCON | TS1001 | PNEUMERCATOR | LC1000 | No | No | No |  |  | No | [5 empty] | No |  |  | Yes |  | No | No | No |  | No Dispensers | [12 empty] | No | Yes | Yes | Yes | Yes | No | No | Yes | No | No | No | Yes | [7 empty] | TRAINING OUTLINE FOR UNDERGROUND STORAGE TANK | Yes |  | Jeff Kingston | General Manager | Omar Arias | Operations Superintendent | Tank Owner/Operator |  | Jeff Kingston | General Manager | 2022-12-27 10:39 | 2023-01-17 10:07 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032526 | 21-000-600235 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - Trestle Glen PS | 500 Tiburon Boulevard | Tiburon | 94920 | UST Removal | 1 | 10032526-001 | Owens Corning | A Stand-alone Tank | 550 | 1982-01-01 | 2014-06-30 |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Conventional Suction | Fiberglass |  | None |  | None | Steel |  | None |  | None | None |  | None |  | None |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: Yes; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Chris Monti; UST Tank Certification / Applicant Information 472: Chief Plant Operator; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: Yes; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: Yes; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: No; Personnel Responsibilities 490-72: Mark Grushayev; Personnel Responsibilities 490-73: WWTP Manager; Personnel Responsibilities 490-74: Chris Monti; Personnel Responsibilities 490-75: CPO | 2017-02-27 14:20 | 2018-01-17 09:21 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032529 | 21-000-600236 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - Salt Works PS | 241 Tiburon Blvd | Tiburon | 94920 | UST Removal | 1 | 10032529-001 | Owens Corning | A Stand-alone Tank | 500 | 1982-01-01 | 2020-02-12 |  | 1 | 550- gallon single-walled fiberglass UST removed on 2/12/2020 and piping was removed and capped at building | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Conventional Suction | Steel |  | None |  | None | Steel |  | None |  | None | None |  | None |  | Fiberglass |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: Yes; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Chris Monti; UST Tank Certification / Applicant Information 472: Chief Plant Operator; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: Yes; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: No; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: Yes; Recordkeeping 490-68f: No; Recordkeeping 490-68g: Yes; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Mark Grushayev; Personnel Responsibilities 490-73: Wastewater Treatment Manager; Personnel Responsibilities 490-74: Chris Monti; Personnel Responsibilities 490-75: Operations Supervisor; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Mark Grushayev; UST Monitoring Plan Certification / Applicant Information 490-79: WWT Manager | 2020-02-13 14:24 | 2020-02-13 14:39 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032532 | 21-000-600237 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - WWTP | 450 Sycamore Avenue | Mill Valley | 94941 | UST Removal | 1 | 10032532-001 | Owens Corning | A Stand-alone Tank | 12000 | 1982-01-01 | 2018-11-01 |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Other | Conventional Suction | Steel |  | Other |  | None | Steel |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Chris Monti; UST Tank Certification / Applicant Information 472: Chief Plant Operator; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: Pneumercator TMS2000; Automatic Tank Gauging 490-13: RA-200; Automatic Tank Gauging 490-14: Pneumercator; Automatic Tank Gauging 490-15: 4505-104-25; Automatic Tank Gauging 490-16: Daily/Nightly; Automatic Tank Gauging 490-18: 0.1 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: Yes; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: No; Personnel Responsibilities 490-72: Mark Grushayev; Personnel Responsibilities 490-73: Wastewater Treatment Manager; Personnel Responsibilities 490-74: Chris Monti; Personnel Responsibilities 490-75: Operations Supervisor; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Chris Monti; UST Monitoring Plan Certification / Applicant Information 490-79: Chief Plant Opertor | 2018-11-14 13:19 | 2018-11-15 14:59 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032538 | 21-000-600918 | AU Energy LLC | 90129649 | Enfrente Shell #113 | 401 Enfrente Rd | Novato | 94949 | Confirmed/Updated Information | 1 | 10032538-001 | Owens Corning | A Stand-alone Tank | 10000 | 1986-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | No | No | No |  |  | Yes | Veeder Root | PLLD | 0.2 GPH | No | No | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Flapper valve overfill alarm set at 90%. Elect. sensor in dsipenser with positive shut down only. TLM sensors 794380-208. | Kris Goyal | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 14:33 | 2023-11-09 13:02 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032538 | 21-000-600918 | AU Energy LLC | 90129649 | Enfrente Shell #113 | 401 Enfrente Rd | Novato | 94949 | Confirmed/Updated Information | 3 | 10032538-003 | Owens Corning | A Stand-alone Tank | 10000 | 1986-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | No | No | No |  |  | Yes | Veeder Root | PLLD | 0.2 GPH | No | No | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Flapper valve overfill alarm set at 90%. Elect. sensor in dsipenser with positive shut down only. TLM sensors 794380-208. | Kris Goyal | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 14:33 | 2023-11-09 13:02 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032538 | 21-000-600918 | AU Energy LLC | 90129649 | Enfrente Shell #113 | 401 Enfrente Rd | Novato | 94949 | Confirmed/Updated Information | 2 | 10032538-002 | Owens Corning | A Stand-alone Tank | 10000 | 1986-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | No | No | No |  |  | Yes | Veeder Root | PLLD | 0.2 GPH | No | No | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | No | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Flapper valve overfill alarm set at 90%. Elect. sensor in dsipenser with positive shut down only. TLM sensors 794380-208. | Kris Goyal | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 14:33 | 2023-11-09 13:02 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032541 | 21-000-600240 | Xtra Oil - dba Shell Oil | 90104047 | Xtra Oil Co. - dba Chevron | 340 Miller Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10032541-001 | Joor | A Stand-alone Tank | 12000 | 1992-11-05 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Jacketed |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Other |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | No |  | Keith Simas | Operations Supervisor | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-420 | Yes | Veeder Root | TLS-350 | Veeder Root | Mag 1 |  |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | [7 empty] | Emergency Response Plan | Yes |  | Ted Simas | Owner | Keith Simas | Operatins Supervisor | Authorized Representative of Owner |  | Keith Simas | Operations Supervisor | 2024-02-22 17:26 | 2024-02-22 18:09 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032541 | 21-000-600240 | Xtra Oil - dba Shell Oil | 90104047 | Xtra Oil Co. - dba Chevron | 340 Miller Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10032541-002 | Joor | A Stand-alone Tank | 12000 | 1992-11-05 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Jacketed |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Other |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | No |  | Keith Simas | Operations Supervisor | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794390-420 | Yes | Veeder Root | TLS-350 | Veeder Root | Mag 1 |  |  |  |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | VMI | LD 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | [7 empty] | Emergency Response Plan | Yes |  | Ted Simas | Owner | Keith Simas | Operatins Supervisor | Authorized Representative of Owner |  | Keith Simas | Operations Supervisor | 2024-02-22 17:26 | 2024-02-22 18:09 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032541 | 21-000-600240 | Xtra Oil - dba Shell Oil | 90104047 | Xtra Oil Co. - dba Chevron | 340 Miller Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10032541-003 | Owens-Corning | A Stand-alone Tank | 10000 | 1972-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | No |  | Keith Simas | Operations Supervisor | Annually |  | New Plan Submitted | No | [5 empty] | Yes | Veeder Root | TLS-350 | Veeder Root | 794390-107 | Daily/Nightly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | Vaporless | LD 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | Yes | No | No | Yes | Yes | [7 empty] | Emergency Response Plan | Yes |  | Ted Simas | Owner | Keith Simas | Operatins Supervisor | Authorized Representative of Owner |  | Keith Simas | Operations Supervisor | 2024-02-22 17:26 | 2024-02-22 18:09 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10032616 | 21-000-600279 | Buck Institute for Age Research | 90104326 | Buck Institute for Research on Aging | 8001 Redwood Boulevard | Novato | 94945 | Confirmed/Updated Information | 1 | 10032616-001 | Fluid Dynamics | A Stand-alone Tank | 6000 | 1998-01-01 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Other |  | Other | Plastic | Single-walled | None |  | None |  | None | None |  | None |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Jay Lewis-Kraitsik; UST Tank Certification / Applicant Information 472: EH&S Manager; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Incon; Continuous Electronic Tank Monitoring 490-8: TS-1000; Continuous Electronic Tank Monitoring 490-9: Incon; Continuous Electronic Tank Monitoring 490-10: DTS; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Incon; Continuous Monitoring of Piping Secondary Containment 490-31: TS-1000; Continuous Monitoring of Piping Secondary Containment 490-32: Incon; Continuous Monitoring of Piping Secondary Containment 490-33: TSP; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: No; Personnel Responsibilities 490-72: Mike Madias; Personnel Responsibilities 490-73: Facilities Manager; Personnel Responsibilities 490-74: Nicole Nannery; Personnel Responsibilities 490-75: EHS/Compliance; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Nicole Nannery; UST Monitoring Plan Certification / Applicant Information 490-79: EH&S Specialist | 2023-09-22 10:54 | 2023-09-22 15:37 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10032634 | 21-000-600919 | AU Energy LLC | 90129649 | DeLong Avenue Shell #112 | 7300 Redwood Blvd | Novato | 94945 | Confirmed/Updated Information | 1 | 10032634-001 | Xerxes | A Stand-alone Tank | 20000 | 2005-07-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-07 16:24 | 2023-11-09 12:48 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032634 | 21-000-600919 | AU Energy LLC | 90129649 | DeLong Avenue Shell #112 | 7300 Redwood Blvd | Novato | 94945 | Confirmed/Updated Information | 2 | 10032634-002 | Xerxes | A Stand-alone Tank | 12000 | 2005-07-20 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-07 16:24 | 2023-11-09 12:48 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032919 | 21-000-600412 | Skywalker Properties (5858/3838 LVR) | 90402109 | Skywalker Properties (5858/3838 LVR) | 5858 Lucas Valley Road | Nicasio | 94946 | Confirmed/Updated Information | Tank 2 | 10032919-002 | Modern Welding Co. Inc. | A Stand-alone Tank | 1000 | 1998-09-03 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Fiberglass; Corrosion Prevention 448a: Yes; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Craig Weichel; UST Tank Certification / Applicant Information 472: Senior Fire Captain; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: Veeder-Root 350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: Veeder-Root #420; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: Veeder-Root; Automatic Tank Gauging 490-13: VR8Y7340-103; Automatic Tank Gauging 490-14: Veeder-Root; Automatic Tank Gauging 490-15: VR8Y7340-103; Automatic Tank Gauging 490-16: Continuous; Automatic Tank Gauging 490-18: 0.1 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: Veeder-Root 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: Veeder-Root#208; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Lou Bouc; Personnel Responsibilities 490-73: Site Facility Engineer; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Craig Weichel; UST Monitoring Plan Certification / Applicant Information 490-79: Senior Fire Captain | 2024-05-13 09:34 | 2024-05-14 09:24 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10032919 | 21-000-600412 | Skywalker Properties (5858/3838 LVR) | 90402109 | Skywalker Properties (5858/3838 LVR) | 5858 Lucas Valley Road | Nicasio | 94946 | Renewal Permit | Tank 1 | 10032919-001 | Modern Welding Co. Inc. | A Stand-alone Tank | 1000 | 1998-09-03 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | Steel |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Fiberglass; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Craig Weichel; UST Tank Certification / Applicant Information 472: Senior Fire Captain; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: Veeder-Root 350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: Veeder-Root #420; Automatic Tank Gauging 490-11: Yes; Automatic Tank Gauging 490-12: Veeder-Root; Automatic Tank Gauging 490-13: VR8Y7340-103; Automatic Tank Gauging 490-14: Veeder-Root; Automatic Tank Gauging 490-15: VR8Y7340-103; Automatic Tank Gauging 490-16: Continuous; Automatic Tank Gauging 490-18: 0.1 GPH; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: Veeder-Root 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: Veeder-Root#208; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: Yes; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Lou Bouc; Personnel Responsibilities 490-73: Site Facility Engineer; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Craig Weichel; UST Monitoring Plan Certification / Applicant Information 490-79: Senior Fire Captain | 2024-05-13 09:34 | 2024-05-14 09:24 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10033030 | 21-000-600459 | Corte Madera Town Center | 90105889 | Town Center Corte Madera | 100 Corte Madera Town Center | Corte Madera | 94925 | UST Removal | 1 | 10033030-001 | Owens-Corning Model | A Stand-alone Tank | 1000 | 1986-01-15 | 2016-10-27 |  | 1 | On 10/27/2016 a 1,000 dbl walled fiberglass tank was removed successfully with analytical below ESLs (lat 37.9296 / long -122.5168) | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | No | No | Double-walled | Conventional Suction | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: Thomas Guilfoyle; UST Tank Certification / Applicant Information 472: Director of Facilities; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Liquid-Filled; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS-300C; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 301; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-300C; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder-Root; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Stan Hoffman; Personnel Responsibilities 490-73: General Manager; Personnel Responsibilities 490-74: Thomas Guilfoyle; Personnel Responsibilities 490-75: Director of Facilities; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Thomas Guilfoyle; UST Monitoring Plan Certification / Applicant Information 490-79: Director of Facilities | 2016-11-07 14:07 | 2016-11-07 14:27 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10033207 | 21-000-601284 | CB Aviation, Inc DBA CB SkyShare | 90713596 | CB Aviation Inc. DBA, CB Sky Share | 351 Airport Road | Novato | 94945 | Confirmed/Updated Information | 2 | 10033207-002 | Trusco | A Stand-alone Tank | 10000 | 1990-06-01 |  |  | 1 |  | Aviation Fueling |  | Aviation Gas |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Single-walled | Pressure | Steel |  | None |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Yes | Yes | No | No Dispensers | None |  | No | No | Yes |  | TJ Neff | Managing Partner | Annually |  | New Plan Submitted | Yes | Dry | Incon | TS-1000 | Incon | TSP-ULS | Yes | Incon | TS-1000 | Incon | TSP-2 | Monthly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Incon | TS-1000 | Beaudreau | 406 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | Yes |  | No | Yes | No |  | No Dispensers | [12 empty] | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Cory Bengtzen | CEO | Robert Battema | General Manager | Tank Owner/Operator |  | TJ Neff | Managing Partner | 2023-06-05 12:16 | 2023-09-21 13:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10033207 | 21-000-601284 | CB Aviation, Inc DBA CB SkyShare | 90713596 | CB Aviation Inc. DBA, CB Sky Share | 351 Airport Road | Novato | 94945 | Confirmed/Updated Information | 1 | 10033207-001 | Trusco | A Stand-alone Tank | 10000 | 1990-06-01 |  |  | 1 |  | Aviation Fueling |  | Jet Fuel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Single-walled | Pressure | Steel |  | None |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Yes | Yes | No | No Dispensers | None |  | No | No | Yes |  | TJ Neff | Managing Partner | Annually |  | New Plan Submitted | Yes | Dry | Incon | TS-1000 | Incon | TSP-ULS | Yes | Incon | TS-1000 | Incon | TSP-2 | Monthly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Incon | TS-1000 | Beaudreau | 406 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | Yes |  | No | Yes | No |  | No Dispensers | [12 empty] | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | Cory Bengtzen | CEO | Robert Battema | General Manager | Tank Owner/Operator |  | TJ Neff | Managing Partner | 2023-06-05 12:16 | 2023-09-21 13:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10033372 | 21-000-600625 | County of Marin | 90404194 | County of Marin/Civic Center-Bldg Eng Tank | 3501 Civic Center Drive | San Rafael | 94903 | UST Removal | 21-000-600625-000001 | 10033372-002 | Modern Welding | A Stand-alone Tank | 8000 | 1999-01-04 | 2018-01-16 |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Other |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Rigid Plastic | [7 empty] | None |  | None |  | None |  | None |  | Yes | No | Yes | No Dispensers |  |  | No | No | No |  | Dean Joyner | Environmental Compliance | Annually |  | Site Plan Previously Submitted | Yes | Dry | Incon | TS-1001 | Incon | TSP-ULS | Yes | Incon | TS-1001 | Incon | TSP-LL2 | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Pressurized | Incon | TS-1001 | Incon | TS-LLD-FE | Yes |  | No |  |  | Yes | Incon | TS-LLD-FE | 0.2 GPH | Yes |  | Yes | Every 3 Years |  | No |  | No | No | No |  | No Dispensers | [12 empty] | Yes | Yes | Yes | Yes | No | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Mike Norton | Building and maintenance manager | Patrick Cunningham | Building and Maintenance supervisor | Tank Owner/Operator |  | Dean Joyner | Environmental Compliance | 2018-01-16 16:36 | 2018-01-17 12:45 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10033372 | 21-000-600625 | County of Marin | 90404194 | County of Marin/Civic Center-Bldg Eng Tank | 3501 Civic Center Drive | San Rafael | 94903 | Confirmed/Updated Information | E-1 | 10033372-001 | Modern Welding | A Stand-alone Tank | 8000 | 1999-01-04 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Jacketed |  | No | No | Yes | No | Double-walled | Pressure | Rigid Plastic |  | Rigid Plastic |  | Double-walled | None |  | None |  | Double-walled | None |  | None |  | Fiberglass |  | Fiberglass |  | Yes | Yes | No | No Dispensers | None |  | No | No | Yes |  | Dean Joyner | Environmental Compliance | Annually |  | Site Plan Previously Submitted | Yes | Dry | Incon | TS-1001 | Incon | TSP-ULS | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Incon | TS-1001 | Incon | TS-ULS | No | No | No |  |  | Yes | Incon | TS-LLD-FE | 0.2 GPH | No | No | Yes | Every 3 Years |  | Yes |  | No | No | No |  | No Dispensers | [12 empty] | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Todd Pressley | Building and Maintenance Manager | Tom Harp | Building Maintenance Supervisor | Tank Owner/Operator |  | Dean Joyner | Environmental Compliance | 2023-12-21 15:27 | 2024-07-17 13:51 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10141619 | 21-000-601189 | Frontier California, Inc. | 90000160 | Frontier California, Inc.: Novato CO | 911 Diablo Avenue | Novato | 94947 | Confirmed/Updated Information | 1 | 10141619-001 | Joor | A Stand-alone Tank | 8000 | 2001-01-12 |  |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Double-walled | Conventional Suction | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | None |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Masood Choudhury; UST Tank Certification / Applicant Information 472: Global EH&S Manager; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 794380-320; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-350; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: Alarm panel is remotely monitored. Overfill alarm is set at 90%.; Personnel Responsibilities 490-72: Masood Choudhury; Personnel Responsibilities 490-73: Global EH&S Manager; Personnel Responsibilities 490-74: Timothy Prade; Personnel Responsibilities 490-75: Environmental Health & Safety; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Masood Choudhury; UST Monitoring Plan Certification / Applicant Information 490-79: Global EH&S Manager | 2023-09-13 13:30 | 2023-11-09 12:57 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10156219 | 21-000-300238 | United Parcel Service, Inc. | 90129202 | UPS - San Rafael | 2985 Kerner Blvd | San Rafael | 94901 | Renewal Permit | 1 | 10156219-001 | Unknown | A Stand-alone Tank | 12000 | 1992-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Rigid Plastic |  | No | No | Yes |  | Carlos Medina | District Plant Engineering Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350, 20.03 | Veeder Root | 302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | Yes | Vaporless | 99LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS-350 | Beaudreau | 406 ls | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | Yes | No | Yes | Yes | [8 empty] | Yes |  | David Bernabe | Buildings & Systems Engineering Supervisor | Drew Potts | Corporate Environmental Coordinator | Authorized Representative of Owner |  | Carlos Medina | District Plant Engineering Manager | 2023-07-17 13:41 | 2023-08-29 09:25 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10156585 | 21-000-600825 | Safeway, Inc. | 90129313 | Safeway Fuel Center #2828 | 5700 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 002C | 10156585-004 | Modern Welding | One in a Compartmented Unit | 8000 | 2008-04-01 |  |  | 3 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Ron Lee | Environmental Manager | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-460 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/857280-100 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Aldo Basurto | Assistant Sales Manager Grocery (Fuel) | Keith Powers | Environmental Compliance Manager | Tank Owner/Operator |  | Ron Lee | Environmental Manager | 2023-12-29 11:14 | 2024-01-31 13:16 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10156585 | 21-000-600825 | Safeway, Inc. | 90129313 | Safeway Fuel Center #2828 | 5700 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 001 | 10156585-001 | Modern Welding | A Stand-alone Tank | 30000 | 2008-04-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Ron Lee | Environmental Manager | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-460 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/857280-100 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Aldo Basurto | Assistant Sales Manager Grocery (Fuel) | Keith Powers | Environmental Compliance Manager | Tank Owner/Operator |  | Ron Lee | Environmental Manager | 2023-12-29 11:14 | 2024-01-31 13:16 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10156585 | 21-000-600825 | Safeway, Inc. | 90129313 | Safeway Fuel Center #2828 | 5700 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 002B | 10156585-003 | Modern Welding | One in a Compartmented Unit | 10000 | 2008-04-01 |  |  | 3 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Ron Lee | Environmental Manager | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-460 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/857280-100 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Aldo Basurto | Assistant Sales Manager Grocery (Fuel) | Keith Powers | Environmental Compliance Manager | Tank Owner/Operator |  | Ron Lee | Environmental Manager | 2023-12-29 11:14 | 2024-01-31 13:16 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10156585 | 21-000-600825 | Safeway, Inc. | 90129313 | Safeway Fuel Center #2828 | 5700 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 002A | 10156585-002 | Modern Welding | One in a Compartmented Unit | 12000 | 2008-04-01 |  |  | 3 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Ron Lee | Environmental Manager | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-460 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/857280-100 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Aldo Basurto | Assistant Sales Manager Grocery (Fuel) | Keith Powers | Environmental Compliance Manager | Tank Owner/Operator |  | Ron Lee | Environmental Manager | 2023-12-29 11:14 | 2024-01-31 13:16 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342432 | 21-000-600275 | County of Marin | 90404194 | County of Marin/Civic Center Garage | 6 Peter Behr Drive | San Rafael | 94903 | Confirmed/Updated Information | Gar- 1 | 10342432-001 | Modern Welding Co., Inc. | A Stand-alone Tank | 10000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Other |  | Yes | No | Yes | No | Double-walled | Conventional Suction | [5 empty] | Steel |  | None |  | None | Steel |  |  |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Saaid Fakhardzadeh | Assistant Director of Public Works | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 300- C | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Patrick McNerney | Environmental Compliance Specialist | Sean Cinelli | Fleet Manager |  |  |  |  | 2024-01-04 08:26 | 2024-07-17 13:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342432 | 21-000-600275 | County of Marin | 90404194 | County of Marin/Civic Center Garage | 6 Peter Behr Drive | San Rafael | 94903 | Confirmed/Updated Information | Gar- 2 | 10342432-002 | Modern Welding Co., Inc. | A Stand-alone Tank | 6000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel | R99 |  | Double Wall | Steel |  | Other |  | Yes | No | Yes | No | Double-walled | Conventional Suction | [5 empty] | Steel |  | None |  | None | Steel |  |  |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Saaid Fakhardzadeh | Assistant Director of Public Works | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 300- C | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Patrick McNerney | Environmental Compliance Specialist | Sean Cinelli | Fleet Manager |  |  |  |  | 2024-01-04 08:26 | 2024-07-17 13:50 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342462 | 21-000-600645 | Matt and Jeff's Car Wash | 90308275 | Matt and Jeff's Car Wash | 125 Vintage Way | Novato | 94945 | Renewal Permit | 2 | 10342462-002 | Xerxes | One in a Compartmented Unit | 12000 | 2003-05-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | Yes | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Other |  | No | No | Yes |  | Matt Broderick | Treasurer/Secretary | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder-Root | TLS-350 | Veeder-Root | VR-301 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes |  | Veeder-Root | TLS-350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Vaporless | LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nick Zagorov | Owner - Eco Check |  |  | Facility Owner/Operator |  | Matt Broderick | Treasurer/Secretary | 2022-08-23 12:46 | 2023-08-10 12:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342462 | 21-000-600645 | Matt and Jeff's Car Wash | 90308275 | Matt and Jeff's Car Wash | 125 Vintage Way | Novato | 94945 | Renewal Permit | 3 | 10342462-003 | Xerxes | A Stand-alone Tank | 20000 | 2003-05-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | Yes | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Other |  | No | No | Yes |  | Matt Broderick | Treasurer/Secretary | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder-Root | TLS-350 | Veeder-Root | VR-301 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes |  | Veeder-Root | TLS-350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Vaporless | LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nick Zagorov | Owner - Eco Check |  |  | Facility Owner/Operator |  | Matt Broderick | Treasurer/Secretary | 2022-08-23 12:46 | 2023-08-10 12:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342462 | 21-000-600645 | Matt and Jeff's Car Wash | 90308275 | Matt and Jeff's Car Wash | 125 Vintage Way | Novato | 94945 | Renewal Permit | 1 | 10342462-001 | Xerxes | One in a Compartmented Unit | 8000 | 2003-05-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | Yes | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Other |  | No | No | Yes |  | Matt Broderick | Treasurer/Secretary | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder-Root | TLS-350 | Veeder-Root | VR-301 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes |  | Veeder-Root | TLS-350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Vaporless | LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder-Root | TLS-350 | Veeder-Root | VR-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Nick Zagorov | Owner - Eco Check |  |  | Facility Owner/Operator |  | Matt Broderick | Treasurer/Secretary | 2022-08-23 12:46 | 2023-08-10 12:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342474 | 21-000-600653 | Bridgeway Gas | 90308284 | Bridgeway Gas | 1103 Bridgeway | Sausalito | 94965 | Renewal Permit | 1 Unleaded 87 | 10342474-001 | Xerxes | A Stand-alone Tank | 10000 | 1981-04-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Yes | No | Yes | Single-walled | Fiberglass |  | No | No | No |  | Sandra Mann | facility owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag Probe | Monthly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 205 | Yes | Yes | Yes | VMI | 99 LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 / 205 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Sandra Mann | facility owner | David Mann | facility owner | Facility Owner/Operator |  | Sandra Mann | facility owner | 2024-01-17 13:23 | 2024-01-17 14:44 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342474 | 21-000-600653 | Bridgeway Gas | 90308284 | Bridgeway Gas | 1103 Bridgeway | Sausalito | 94965 | Renewal Permit | 3 Premium 91 | 10342474-003 | Xerxes | A Stand-alone Tank | 10000 | 1981-04-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Yes | No | Yes | Single-walled | Fiberglass |  | No | No | No |  | Sandra Mann | facility owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag Probe | Monthly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | VMI | 99 LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 / 205 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Sandra Mann | facility owner | David Mann | facility owner | Facility Owner/Operator |  | Sandra Mann | facility owner | 2024-01-17 13:23 | 2024-01-17 14:44 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342474 | 21-000-600653 | Bridgeway Gas | 90308284 | Bridgeway Gas | 1103 Bridgeway | Sausalito | 94965 | Renewal Permit | 2 89 Unleaded | 10342474-002 | Xerxes | A Stand-alone Tank | 10000 | 1981-04-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Midgrade Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | Steel |  | None |  | Yes | No | Yes | Single-walled | Fiberglass |  | No | No | No |  | Sandra Mann | facility owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | Mag Probe | Monthly |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 205 | Yes | Yes | Yes | VMI | 99 LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 / 205 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Sandra Mann | facility owner | David Mann | facility owner | Facility Owner/Operator |  | Sandra Mann | facility owner | 2024-01-17 13:23 | 2024-01-17 14:44 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342489 | 21-000-600664 | Bolinas Gas Station | 90308299 | Bolinas Gas Station | 6 Wharf Road | Bolinas | 94924 | Renewal Permit | 87 | 10342489-001 | Modern Welding | One in a Compartmented Unit | 8000 | 2000-04-01 |  |  | 3 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Steel |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Steel |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | No | No | Single-walled | Fiberglass |  | No | No | Yes |  | Albert Foreman | Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | VMI | 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Albert Foreman | Manager | Debbie Morrison | Manager | Authorized Representative of Owner |  | Albert Foreman | Manager | 2023-11-10 10:58 | 2023-11-19 21:54 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342489 | 21-000-600664 | Bolinas Gas Station | 90308299 | Bolinas Gas Station | 6 Wharf Road | Bolinas | 94924 | Renewal Permit | diesel | 10342489-003 | Modern Welding | One in a Compartmented Unit | 3000 | 2000-04-01 |  |  | 3 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Steel |  | Yes | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Steel |  | None |  | None | None |  | None |  | Steel |  | None |  | Yes | No | No | Single-walled | Fiberglass |  | No | No | Yes |  | Albert Foreman | Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | VMI | 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Albert Foreman | Manager | Debbie Morrison | Manager | Authorized Representative of Owner |  | Albert Foreman | Manager | 2023-11-10 10:58 | 2023-11-19 21:54 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342489 | 21-000-600664 | Bolinas Gas Station | 90308299 | Bolinas Gas Station | 6 Wharf Road | Bolinas | 94924 | Renewal Permit | 91 | 10342489-002 | Modern Welding | One in a Compartmented Unit | 4000 | 2000-04-01 |  |  | 3 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Steel |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Steel |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | No | No | Single-walled | Fiberglass |  | No | No | Yes |  | Albert Foreman | Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | Yes | Yes | Yes | VMI | 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Albert Foreman | Manager | Debbie Morrison | Manager | Authorized Representative of Owner |  | Albert Foreman | Manager | 2023-11-10 10:58 | 2023-11-19 21:54 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342510 | 21-000-600721 | Salkhi Family Holdings Inc. | 90130033 | 570 Redwood Valero | 570 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10342510-002 | Modern Welding | One in a Compartmented Unit | 10000 | 2001-07-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Amin Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Ali Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Amin Salkhi | President | 2023-12-08 13:01 | 2024-01-08 12:03 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342510 | 21-000-600721 | Salkhi Family Holdings Inc. | 90130033 | 570 Redwood Valero | 570 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10342510-003 | Modern Welding | One in a Compartmented Unit | 5000 | 2001-07-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Amin Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Vaporless VMI | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Ali Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Amin Salkhi | President | 2023-12-08 13:01 | 2024-01-08 12:03 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342510 | 21-000-600721 | Salkhi Family Holdings Inc. | 90130033 | 570 Redwood Valero | 570 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10342510-001 | Modern Welding | A Stand-alone Tank | 15000 | 2001-07-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Amin Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Vaporless VMI | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Ali Salkhi | President | Samuel "Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Amin Salkhi | President | 2023-12-08 13:01 | 2024-01-08 12:03 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342513 | 21-000-600722 | Salkhi Family Holdings Inc. | 90130033 | Mill Valley Chevron | 5 Ashford Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10342513-001 | FLUID CONTAINMENT | A Stand-alone Tank | 12000 | 1999-09-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-407 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Samuel 'Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-12-08 12:46 | 2024-01-08 11:59 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342513 | 21-000-600722 | Salkhi Family Holdings Inc. | 90130033 | Mill Valley Chevron | 5 Ashford Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10342513-003 | FLUID CONTAINMENT | A Stand-alone Tank | 5000 | 1999-09-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-407 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Samuel 'Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-12-08 12:46 | 2024-01-08 11:59 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342513 | 21-000-600722 | Salkhi Family Holdings Inc. | 90130033 | Mill Valley Chevron | 5 Ashford Avenue | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10342513-002 | FLUID CONTAINMENT | A Stand-alone Tank | 12000 | 1999-09-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-407 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Arash Salkhi | President | Samuel 'Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2023-12-08 12:46 | 2024-01-08 11:59 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342591 | 21-000-601313 | AS Convenience & Energy Inc. | 90379039 | STRAWBERRY CHEVRON FOOD MART | 580 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | T2 | 10342591-002 | Xerxes | One in a Compartmented Unit | 12000 | 2007-04-10 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304/330020-480 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304 | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:17 | 2024-01-08 08:58 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342591 | 21-000-601313 | AS Convenience & Energy Inc. | 90379039 | STRAWBERRY CHEVRON FOOD MART | 580 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | T4 | 10342591-004 | Xerxes | A Stand-alone Tank | 500 | 2007-04-10 |  |  | 1 |  | Other |  | Other Non-petroleum |  | oily water | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Other | 23 CCR §2636(a)(3) Suction | None |  | None |  | None | None |  | None |  | None | None |  | None |  | None |  | None |  | Fill Components Installed 451-a: No; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: VERDAN ABREGANA; UST Tank Certification / Applicant Information 472: PROJECT MANAGER; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-8: TLS 350R; Continuous Electronic Tank Monitoring 490-9: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-10: 794390-407; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-69i: UST Monitoring Plan, Operating Manual; Training 490-70: Yes; Personnel Responsibilities 490-72: Arash Salkhi; Personnel Responsibilities 490-73: President; Personnel Responsibilities 490-74: Samuel Spencer; Personnel Responsibilities 490-75: Regional Manager; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: VERDAN ABREGANA; UST Monitoring Plan Certification / Applicant Information 490-79: PROJECT MANAGER | 2023-12-08 12:17 | 2024-01-08 08:58 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342591 | 21-000-601313 | AS Convenience & Energy Inc. | 90379039 | STRAWBERRY CHEVRON FOOD MART | 580 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | T3 | 10342591-003 | Xerxes | One in a Compartmented Unit | 8000 | 2007-04-10 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304/ 330020-480 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304 | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:17 | 2024-01-08 08:58 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342591 | 21-000-601313 | AS Convenience & Energy Inc. | 90379039 | STRAWBERRY CHEVRON FOOD MART | 580 Redwood Highway | Mill Valley | 94941 | Confirmed/Updated Information | T1 | 10342591-001 | Xerxes | A Stand-alone Tank | 20000 | 2007-04-10 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | VERDAN ABREGANA | PROJECT MANAGER | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304/330020-485 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304 | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel Spencer | Regional Manager | Authorized Representative of Owner |  | VERDAN ABREGANA | PROJECT MANAGER | 2023-12-08 12:17 | 2024-01-08 08:58 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342663 | 21-000-601292 | GAWFCO Enterprises, Inc. | 90365647 | RedHill Convenience & Fuel | 930 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 2 | 10342663-002 | Modern Welding | A Stand-alone Tank | 12000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 794380-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: VMI; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-55: Mechanical; Under Dispenser Containment (UDC) Monitoring 490-56: Float & Chain; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: No; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-69i: UST Monitoring Plan, Operating Manuals; Training 490-70: Yes; Personnel Responsibilities 490-72: Nick Ahmadi; Personnel Responsibilities 490-73: Co-Dealer; Personnel Responsibilities 490-74: Nader Ahmadi; Personnel Responsibilities 490-75: Co-Dealer | 2023-11-07 10:31 | 2024-03-19 12:00 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342663 | 21-000-601292 | GAWFCO Enterprises, Inc. | 90365647 | RedHill Convenience & Fuel | 930 Sir Francis Drake Boulevard | San Anselmo | 94960 | Confirmed/Updated Information | 1 | 10342663-001 | Modern Welding | A Stand-alone Tank | 12000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 794380-420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS 350; Continuous Monitoring of Piping Secondary Containment 490-32: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-33: 794380-208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: VMI; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-55: Mechanical; Under Dispenser Containment (UDC) Monitoring 490-56: Float & Chain; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: No; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-69i: UST Monitoring Plan, Operating Manuals; Training 490-70: Yes; Personnel Responsibilities 490-72: Nick Ahmadi; Personnel Responsibilities 490-73: Co-Dealer; Personnel Responsibilities 490-74: Nader Ahmadi; Personnel Responsibilities 490-75: Co-Dealer | 2023-11-07 10:31 | 2024-03-19 12:00 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342681 | 21-000-600823 | HQ Fuels | 90308479 | HQ Fuels | 251 Shoreline Highway | Mill Valley | 94941 | Confirmed/Updated Information | 3 | 10342681-003 | Xeres | One in a Compartmented Unit | 12000 | 2002-12-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Louis Saadeh | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 301 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Veeder Root | Series 8484 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Louis Saadeh | President | Morelio Baten | Manager | Facility Owner/Operator |  | Louis Saadeh | President | 2024-02-11 21:35 | 2024-02-12 07:48 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342681 | 21-000-600823 | HQ Fuels | 90308479 | HQ Fuels | 251 Shoreline Highway | Mill Valley | 94941 | Confirmed/Updated Information | 2 | 10342681-002 | Xeres | One in a Compartmented Unit | 10000 | 2002-12-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Louis Saadeh | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 301 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Veeder Root | Series 8484 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Louis Saadeh | President | Morelio Baten | Manager | Facility Owner/Operator |  | Louis Saadeh | President | 2024-02-11 21:35 | 2024-02-12 07:48 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342681 | 21-000-600823 | HQ Fuels | 90308479 | HQ Fuels | 251 Shoreline Highway | Mill Valley | 94941 | Confirmed/Updated Information | 1 | 10342681-001 | Xeres | A Stand-alone Tank | 20000 | 2002-12-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Louis Saadeh | owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 301 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Veeder Root | Series 8484 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Louis Saadeh | President | Morelio Baten | Manager | Facility Owner/Operator |  | Louis Saadeh | President | 2024-02-11 21:35 | 2024-02-12 07:48 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342681 | 21-000-600823 | HQ Fuels | 90308479 | HQ Fuels | 251 Shoreline Highway | Mill Valley | 94941 | Confirmed/Updated Information | 4 | 10342681-004 | Joor | A Stand-alone Tank | 500 | 1988-05-01 |  |  | 1 |  | Hazardous Waste (includes used oil) |  | Used Oil |  |  | Double Wall | Fiberglass |  | Steel |  | Yes | Yes | No | No | Other | Gravity | None |  | None |  | None | None |  | None |  | None | None |  | None |  | None |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Louis Saadeh; UST Tank Certification / Applicant Information 472: owner; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: TLS 350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Louis Saadeh; Personnel Responsibilities 490-73: Owner; Personnel Responsibilities 490-74: Morelio Baten; Personnel Responsibilities 490-75: Manager; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Louis Saadeh; UST Monitoring Plan Certification / Applicant Information 490-79: owner | 2024-02-11 21:35 | 2024-02-12 07:48 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342696 | 21-000-600838 | Power Petroleum Corporation | 90308494 | Power Petroleum Corporation | 1320 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 4-Regular | 10342696-004 | Unknown | One in a Compartmented Unit | 5044 | 1899-12-31 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | [13 empty] | Yes | No | No | Single-walled | Steel |  | No | No | Yes |  | Robert Poquez | Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 |  |  | Yes |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Evelyn A. Poquez | CEO | Robert Poquez | Manager | Facility Owner/Operator |  | Evelyn A. Poquez | CEO | 2023-12-22 11:20 | 2023-12-22 11:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342696 | 21-000-600838 | Power Petroleum Corporation | 90308494 | Power Petroleum Corporation | 1320 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 3-Diesel | 10342696-003 | unknown | One in a Compartmented Unit | 7128 | 1899-12-31 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | None |  | None |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | Yes |  | Robert Poquez | Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 |  |  | Yes |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Evelyn A. Poquez | CEO | Robert Poquez | Manager | Facility Owner/Operator |  | Evelyn A. Poquez | CEO | 2023-12-22 11:20 | 2023-12-22 11:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342696 | 21-000-600838 | Power Petroleum Corporation | 90308494 | Power Petroleum Corporation | 1320 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 1-Premium | 10342696-001 | unknown | One in a Compartmented Unit | 7128 | 1899-12-31 |  |  | 2 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | None | Steel |  |  |  | None |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Robert Poquez | owner/operator | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 |  |  | Yes |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Evelyn A. Poquez | CEO | Robert Poquez | Manager | Facility Owner/Operator |  | Evelyn A. Poquez | CEO | 2023-12-22 11:20 | 2023-12-22 11:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342696 | 21-000-600838 | Power Petroleum Corporation | 90308494 | Power Petroleum Corporation | 1320 Second Street | San Rafael | 94901 | Confirmed/Updated Information | 2-Regular | 10342696-002 | unknown | One in a Compartmented Unit | 7128 | 1899-12-31 |  |  | 2 |  | Motor Vehicle Fueling |  | Midgrade Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | Steel |  | None |  | None |  | None |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | Yes |  | Robert Poquez | Manager | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | Veeder Root TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 |  |  | Yes |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  | Veeder Root | TLS 350 | Veeder Root | 847990-001 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Evelyn A. Poquez | CEO | Robert Poquez | Manager | Facility Owner/Operator |  | Evelyn A. Poquez | CEO | 2023-12-22 11:20 | 2023-12-22 11:42 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342789 | 21-000-600888 | Northgate Gas | 90308581 | Northgate Gas | 77 San Pablo Avenue | San Rafael | 94903 | Renewal Permit | 3 | 10342789-003 | Owen/Corning | A Stand-alone Tank | 6000 | 1984-08-27 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Single-walled | Steel |  | None |  | Steel |  | None |  | Yes | No | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Shahram Shahnazi | Shahram Shahnazi | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | MAG Plus | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Vaporless | 99 LD-2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Shahram Shahnazi | owner | Farah Karaijh | cashier | Authorized Representative of Owner |  | Shahram Shahnazi | Business Owner | 2023-12-28 12:00 | 2023-12-28 12:17 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342789 | 21-000-600888 | Northgate Gas | 90308581 | Northgate Gas | 77 San Pablo Avenue | San Rafael | 94903 | Renewal Permit | 2 | 10342789-002 | Owen/Corning | A Stand-alone Tank | 6000 | 1984-08-27 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Single-walled | Steel |  | None |  | Steel |  | None |  | Yes | No | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Shahram Shahnazi | Business Owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | MAG Plus | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Veeder Root | Red Jacket FX2V | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Shahram Shahnazi | owner | Farah Karaijh | cashier | Authorized Representative of Owner |  | Shahram Shahnazi | Business Owner | 2023-12-28 12:00 | 2023-12-28 12:17 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342789 | 21-000-600888 | Northgate Gas | 90308581 | Northgate Gas | 77 San Pablo Avenue | San Rafael | 94903 | Renewal Permit | 1 | 10342789-001 | Owen/Corning | A Stand-alone Tank | 6000 | 1984-08-27 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | No | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | Steel |  | Single-walled | Steel |  | None |  | Steel |  | None |  | Yes | No | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Shahram Shahnazi | Business Owner | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | Veeder Root | TLS 350 | Veeder Root | MAG Plus | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | Veeder Root | Red Jacket FX2V | No | [5 empty] | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Shahram Shahnazi | owner | Farah Karaijh | cashier | Authorized Representative of Owner |  | Shahram Shahnazi | Business Owner | 2023-12-28 12:00 | 2023-12-28 12:17 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342822 | 21-000-601067 | A&A GAS INC | 90308611 | Marin Gas & Auto Service | 600 Magnolia Avenue | Larkspur | 94939 | Renewal Permit | 1 | 10342822-001 | TRUSCO | A Stand-alone Tank | 10000 | 1995-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Other |  | None | Fiberglass |  | None |  | Fiberglass |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Rigid Plastic; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: GHULAM ALI; UST Tank Certification / Applicant Information 472: PRESIDENT; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD-2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: ALU GHULAM; Personnel Responsibilities 490-73: OWNER; Personnel Responsibilities 490-74: Lucio; Personnel Responsibilities 490-75: SITE MANAGER; UST Monitoring Plan Certification / Applicant Information 490-78: GHULAM ALI; UST Monitoring Plan Certification / Applicant Information 490-79: PRESIDENT | 2023-11-08 16:16 | 2023-11-08 16:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342822 | 21-000-601067 | A&A GAS INC | 90308611 | Marin Gas & Auto Service | 600 Magnolia Avenue | Larkspur | 94939 | Confirmed/Updated Information | 3 | 10342822-003 | TRUSCO | A Stand-alone Tank | 10000 | 1995-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Other |  | None | Fiberglass |  | None |  | Fiberglass |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Rigid Plastic; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: GHULAM ALI; UST Tank Certification / Applicant Information 472: PRESIDENT; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: Yes; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Ghulam Ali; Personnel Responsibilities 490-73: Owner; Personnel Responsibilities 490-74: Lucio; Personnel Responsibilities 490-75: SITE MANAGER; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: GHULAM ALI; UST Monitoring Plan Certification / Applicant Information 490-79: PRESIDENT | 2023-11-08 16:16 | 2023-11-08 16:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342822 | 21-000-601067 | A&A GAS INC | 90308611 | Marin Gas & Auto Service | 600 Magnolia Avenue | Larkspur | 94939 | Confirmed/Updated Information | 4 | 10342822-004 | TRUSCO | A Stand-alone Tank | 500 | 1995-10-01 |  |  | 1 |  | Hazardous Waste (includes used oil) |  | Used Oil |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Other |  | None | Fiberglass |  | None |  | Fiberglass |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Rigid Plastic; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: GHULAM ALI; UST Tank Certification / Applicant Information 472: PRESIDENT; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: Yes; Continuous Monitoring of Piping Secondary Containment 490-35: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Ghulam Ali; Personnel Responsibilities 490-73: Owner; Personnel Responsibilities 490-74: Lucio; Personnel Responsibilities 490-75: SITE MANAGER; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: GHULAM ALI; UST Monitoring Plan Certification / Applicant Information 490-79: PRESIDENT | 2023-11-08 16:16 | 2023-11-08 16:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342822 | 21-000-601067 | A&A GAS INC | 90308611 | Marin Gas & Auto Service | 600 Magnolia Avenue | Larkspur | 94939 | Confirmed/Updated Information | 2 | 10342822-002 | TRUSCO | A Stand-alone Tank | 10000 | 1995-10-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Other |  | None | Fiberglass |  | None |  | Fiberglass |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Rigid Plastic; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; UST Tank Certification / Applicant Information 471: GHULAM ALI; UST Tank Certification / Applicant Information 472: PRESIDENT; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder-Root; Continuous Electronic Tank Monitoring 490-8: TLS350; Continuous Electronic Tank Monitoring 490-9: Veeder-Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: TLS350; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER-ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: Yes; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-37: Vaporless; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-38: LD2000; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Float and Chain Assembly; Under Dispenser Containment (UDC) Monitoring 490-62: Yes; Under Dispenser Containment (UDC) Monitoring 490-63: Single-walled; Under Dispenser Containment (UDC) Monitoring 490-64b: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Ghulam Ali; Personnel Responsibilities 490-73: Owner; Personnel Responsibilities 490-74: Lucio; Personnel Responsibilities 490-75: SITE MANAGER; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: GHULAM ALI; UST Monitoring Plan Certification / Applicant Information 490-79: PRESIDENT | 2023-11-08 16:16 | 2023-11-08 16:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342855 | 21-000-600916 | AU Energy LLC | 90129649 | Miwok Shell #109 | 7473 Redwood Blvd | Novato | 94945 | Confirmed/Updated Information | 2 | 10342855-002 | Xerxes | One in a Compartmented Unit | 12000 | 2016-08-29 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS- 350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 14:54 | 2023-12-21 13:38 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342855 | 21-000-600916 | AU Energy LLC | 90129649 | Miwok Shell #109 | 7473 Redwood Blvd | Novato | 94945 | Confirmed/Updated Information | 1 | 10342855-001 | Xerxes | A Stand-alone Tank | 20000 | 2016-08-29 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS- 350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 14:54 | 2023-12-21 13:38 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342855 | 21-000-600916 | AU Energy LLC | 90129649 | Miwok Shell #109 | 7473 Redwood Blvd | Novato | 94945 | Confirmed/Updated Information | 3 | 10342855-003 | Xerxes | One in a Compartmented Unit | 8000 | 2016-08-29 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS- 350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 14:54 | 2023-12-21 13:38 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342858 | 21-000-600917 | AU Energy LLC | 90129649 | Novato Shell #110 | 1390 S. Novato Blvd | Novato | 94947 | Confirmed/Updated Information | 3 | 10342858-003 | Xerxes | One in a Compartmented Unit | 8000 | 2015-06-22 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 16:27 | 2023-11-09 13:59 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342858 | 21-000-600917 | AU Energy LLC | 90129649 | Novato Shell #110 | 1390 S. Novato Blvd | Novato | 94947 | Confirmed/Updated Information | 1 | 10342858-001 | Xerxes | A Stand-alone Tank | 20000 | 2015-06-22 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 16:27 | 2023-11-09 13:59 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342858 | 21-000-600917 | AU Energy LLC | 90129649 | Novato Shell #110 | 1390 S. Novato Blvd | Novato | 94947 | Confirmed/Updated Information | 2 | 10342858-002 | Xerxes | One in a Compartmented Unit | 12000 | 2015-06-22 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 16:27 | 2023-11-09 13:59 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342870 | 21-000-600920 | AU Energy LLC | 90129649 | West Novato Shell #111 | 2085 Novato Boulevard | Novato | 94947 | Confirmed/Updated Information | 2 | 10342870-002 | Xerxes | One in a Compartmented Unit | 12000 | 2014-10-14 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 16:32 | 2023-11-09 12:51 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342870 | 21-000-600920 | AU Energy LLC | 90129649 | West Novato Shell #111 | 2085 Novato Boulevard | Novato | 94947 | Confirmed/Updated Information | 1 | 10342870-001 | Xerxes | A Stand-alone Tank | 20000 | 2014-10-24 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 16:32 | 2023-11-09 12:51 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342870 | 21-000-600920 | AU Energy LLC | 90129649 | West Novato Shell #111 | 2085 Novato Boulevard | Novato | 94947 | Confirmed/Updated Information | 3 | 10342870-003 | Xerxes | One in a Compartmented Unit | 8000 | 2014-10-14 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2023-11-03 16:32 | 2023-11-09 12:51 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342876 | 21-000-600922 | AU Energy LLC | 90129649 | Northgate Shell #118 | 950 Del Presidio Boulevard | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10342876-002 | Xerxes | One in a Compartmented Unit | 8000 | 2012-12-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 (shared w/ Diesel tank) | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2024-06-18 14:32 | 2024-07-05 14:45 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342876 | 21-000-600922 | AU Energy LLC | 90129649 | Northgate Shell #118 | 950 Del Presidio Boulevard | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10342876-003 | Xerxes | One in a Compartmented Unit | 7000 | 2012-12-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 (shared with 91 tank) | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2024-06-18 14:32 | 2024-07-05 14:45 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342876 | 21-000-600922 | AU Energy LLC | 90129649 | Northgate Shell #118 | 950 Del Presidio Boulevard | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10342876-001 | Xerxes | A Stand-alone Tank | 15000 | 2012-12-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-304/794380-208 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2024-06-18 14:32 | 2024-07-05 14:45 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342879 | 21-000-600923 | AU Energy LLC | 90129649 | Drake Shell #106 | 295 Sir Francis Drake Boulevard | Greenbrae | 94904 | Confirmed/Updated Information | 2 | 10342879-002 | Owens Corning | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2024-07-17 16:54 | 2024-07-22 13:14 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342879 | 21-000-600923 | AU Energy LLC | 90129649 | Drake Shell #106 | 295 Sir Francis Drake Boulevard | Greenbrae | 94904 | Confirmed/Updated Information | 3 | 10342879-003 | Owens Corning | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2024-07-17 16:54 | 2024-07-22 13:14 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342879 | 21-000-600923 | AU Energy LLC | 90129649 | Drake Shell #106 | 295 Sir Francis Drake Boulevard | Greenbrae | 94904 | Confirmed/Updated Information | 1 | 10342879-001 | Owens Corning | A Stand-alone Tank | 12000 | 1996-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2024-07-17 16:54 | 2024-07-22 13:14 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | Confirmed/Updated Information | 4 | 10342882-001 | Xerxes | A Stand-alone Tank | 20000 | 2017-11-03 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-450 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-450 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-450 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager |  |  |  |  | 2024-07-03 11:45 | 2024-07-24 14:00 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | Confirmed/Updated Information | 5 | 10342882-002 | Xerxes | One in a Compartmented Unit | 12000 | 2017-11-03 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-450 | Veeder Root | 794380-303 (shared w/ Diesel tank) | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-450 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-450 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager |  |  |  |  | 2024-07-03 11:45 | 2024-07-24 14:00 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | Confirmed/Updated Information | 6 | 10342882-003 | Xerxes | One in a Compartmented Unit | 12000 | 2017-11-03 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-450 | Veeder Root | 794380-303 (shared with 91 tank) | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-450 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-450 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager |  |  |  |  | 2024-07-03 11:45 | 2024-07-24 14:00 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | UST Removal | 2 | 10342882-005 | Owens Corning | A Stand-alone Tank | 12000 | 1990-01-01 | 2017-10-18 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | Overfill alarm is set at 90% shut off is set at 95% | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2018-01-04 13:37 | 2018-02-13 09:49 | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | UST Removal | 3 | 10342882-004 | Owens Corning | A Stand-alone Tank | 12000 | 1990-01-01 | 2017-10-18 |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | Overfill alarm is set at 90% shut off is set at 95% | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2018-01-04 13:37 | 2018-02-13 09:49 | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10342882 | 21-000-600924 | AU Energy LLC | 90129649 | Irwin Shell #117 | 834 Irwin Street | San Rafael | 94901 | UST Removal | 1 | 10342882-006 | Owens Corning | A Stand-alone Tank | 12000 | 1990-01-01 | 2017-10-18 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | Overfill alarm is set at 90% shut off is set at 95% | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2018-01-04 13:37 | 2018-02-13 09:49 | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | UST Removal | 1 | 10342885-001 | Fluid Containment | A Stand-alone Tank | 8000 | 1998-01-01 | 2019-08-07 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | No | No | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | TLM Sump Sensor 794380-208 | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2021-01-14 14:57 | 2021-01-19 11:19 | Tracey Nguyen | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | UST Removal | 3 | 10342885-003 | Fluid Containment | A Stand-alone Tank | 8000 | 1998-01-01 | 2019-08-07 |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | No | No | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | TLM Sump Sensor 794380-208 | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2021-01-14 14:57 | 2021-01-19 11:19 | Tracey Nguyen | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | UST Removal | 2 | 10342885-002 | Fluid Containment | A Stand-alone Tank | 8000 | 1998-01-01 | 2019-08-07 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Sunny Goyal | Project Manager | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-302 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | No | No | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | TLM Sump Sensor 794380-208 | Kris Goyal | Territory Manager | Sunny Goyal | Project Manager | Tank Owner/Operator |  | Sunny Goyal | Project Manager | 2021-01-14 14:57 | 2021-01-19 11:19 | Tracey Nguyen | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10342885-004 | Xerxes | A Stand-alone Tank | 20000 | 2019-09-10 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager |  |  |  |  | 2024-06-18 13:58 | 2024-06-24 15:09 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10342885-005 | Xerxes | One in a Compartmented Unit | 12000 | 2019-09-10 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager |  |  |  |  | 2024-06-18 13:58 | 2024-06-24 15:09 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10342885 | 21-000-600925 | AU Energy LLC | 90129649 | 4th Street Shell #119 | 1833 Fourth Street | San Rafael | 94901 | Confirmed/Updated Information | 3 | 10342885-006 | Xerxes | One in a Compartmented Unit | 8000 | 2019-09-10 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304/332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Om Giri | Regional Manager | Sunny Goyal | Project Manager |  |  |  |  | 2024-06-18 13:58 | 2024-06-24 15:09 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10342927 | 21-000-601153 | Apro LLC | 90161914 | United #5651 | 250 Tiburon Boulevard | Tiburon | 94920 | Confirmed/Updated Information | 2 | 10342927-002 | Modern Welding | A Stand-alone Tank | 12000 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Allen Faass | Compliance | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | Yes | VMI | LD 2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Tom Robins | Staff Geologist | Stephanie Ferguson | Compliance Manager | Authorized Representative of Owner |  | Allen Faass | Compliance | 2024-01-18 12:26 | 2024-01-22 01:31 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342927 | 21-000-601153 | Apro LLC | 90161914 | United #5651 | 250 Tiburon Boulevard | Tiburon | 94920 | Confirmed/Updated Information | 1 | 10342927-001 | Modern Welding | A Stand-alone Tank | 12000 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | Fiberglass |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Allen Faass | Compliance | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | Yes | Fe Petro | MLD-STP | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Tom Robins | Staff Geologist | Stephanie Ferguson | Compliance Manager | Authorized Representative of Owner |  | Allen Faass | Compliance | 2024-01-18 12:26 | 2024-01-22 01:31 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342954 | 21-000-600954 | Sausalito Shell | 90308737 | ANABI OIL CORP DBA SAUSALITO SHELL | 2901 Bridgeway | Sausalito | 94965 | Confirmed/Updated Information | 3 | 10342954-003 | Xerxes | A Stand-alone Tank | 12000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Summer Ireifej | Controller | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Richard Miller | Dealer | Jeff Herstik | General Manager | Tank Owner/Operator |  | Summer Ireifej | Controller | 2024-05-06 15:01 | 2024-05-07 15:21 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342954 | 21-000-600954 | Sausalito Shell | 90308737 | ANABI OIL CORP DBA SAUSALITO SHELL | 2901 Bridgeway | Sausalito | 94965 | Confirmed/Updated Information | 1 | 10342954-001 | Xerxes | A Stand-alone Tank | 12000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Summer Ireifej | Controller | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Richard Miller | Dealer | Jeff Herstik | General Manager | Tank Owner/Operator |  | Summer Ireifej | Controller | 2024-05-06 15:01 | 2024-05-07 15:21 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342954 | 21-000-600954 | Sausalito Shell | 90308737 | ANABI OIL CORP DBA SAUSALITO SHELL | 2901 Bridgeway | Sausalito | 94965 | Confirmed/Updated Information | 2 | 10342954-002 | Xerxes | A Stand-alone Tank | 12000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Summer Ireifej | Controller | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Line Leak Detector - 87 tank manifolds | Richard Miller | Dealer | Jeff Herstik | General Manager | Tank Owner/Operator |  | Summer Ireifej | Controller | 2024-05-06 15:01 | 2024-05-07 15:21 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342957 | 21-000-601424 | RADC Enterprises Inc. | 90366556 | Novato Shell | 5821 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 2 | 10342957-002 | Owens Corning | A Stand-alone Tank | 12000 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Summer Ireifej | Controller | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Mojgan Anvari | General Manager | Max Zech | Operations Manager | Tank Owner/Operator |  | Summer Ireifej | Controller | 2023-11-06 16:44 | 2023-11-09 12:52 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342957 | 21-000-601424 | RADC Enterprises Inc. | 90366556 | Novato Shell | 5821 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 3 | 10342957-003 | Owens Corning | A Stand-alone Tank | 12000 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Summer Ireifej | Controller | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Mojgan Anvari | General Manager | Max Zech | Operations Manager | Tank Owner/Operator |  | Summer Ireifej | Controller | 2023-11-06 16:44 | 2023-11-09 12:52 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342957 | 21-000-601424 | RADC Enterprises Inc. | 90366556 | Novato Shell | 5821 Nave Drive | Novato | 94949 | Confirmed/Updated Information | 1 | 10342957-001 | Owens Corning | A Stand-alone Tank | 12000 | 1990-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Summer Ireifej | Controller | Annually |  | Site Plan Previously Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes |  | Mojgan Anvari | General Manager | Max Zech | Operations Manager | Tank Owner/Operator |  | Summer Ireifej | Controller | 2023-11-06 16:44 | 2023-11-09 12:52 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10342990 | 21-000-600969 | North Bay Gas | 90308770 | North Bay Gas | 1789 Sir Francis Drake Boulevard | Fairfax | 94930 | Renewal Permit | 1 | 10342990-001 | Joor Plasteel | A Stand-alone Tank | 12000 | 2001-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Shahram Shahmaz | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | No |  | Shahram Shahmaz | Owner | Farah Karaijh | cashier | Tank Owner/Operator |  | Shahram Shahmaz | Owner | 2023-12-28 12:18 | 2023-12-28 12:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342990 | 21-000-600969 | North Bay Gas | 90308770 | North Bay Gas | 1789 Sir Francis Drake Boulevard | Fairfax | 94930 | Renewal Permit | 2 | 10342990-002 | Joor Plasteel | One in a Compartmented Unit | 8000 | 2001-01-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Shahram Shahmaz | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Shahram Shahmaz | Owner | Farah Karaijh | cashier | Tank Owner/Operator |  | Shahram Shahmaz | Owner | 2023-12-28 12:18 | 2023-12-28 12:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342990 | 21-000-600969 | North Bay Gas | 90308770 | North Bay Gas | 1789 Sir Francis Drake Boulevard | Fairfax | 94930 | Renewal Permit | 3 | 10342990-003 | Joor Plasteel | One in a Compartmented Unit | 4000 | 2001-01-01 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | Yes | No | No | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Shahram Shahmaz | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794390-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | No |  |  | Yes | Veeder Root | Series 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS 350 | Veeder Root | 794380-208 | Yes | Yes | Yes | No | Single-walled |  | Yes | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Shahram Shahmaz | Owner | Farah Karaijh | cashier | Tank Owner/Operator |  | Shahram Shahmaz | Owner | 2023-12-28 12:18 | 2023-12-28 12:26 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342996 | 21-000-601202 | BRENTWOOD GAS & MORE | 90615466 | Corte Madera Gas | 700 Tamalpais Drive | Corte Madera | 94925 | Confirmed/Updated Information | 2 | 10342996-002 | XERXES | A Stand-alone Tank | 12000 | 1999-03-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Fiberglass |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Rajinder Brar | President/Secretary | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 407 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | FE PETRO | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | EPA Guide: Managing Hazardous Waste. EPA Guide: Must for USTs. | Yes |  | Sukhwinder Singh | Facility Operator |  |  | Tank Owner/Operator |  | Rajinder Brar | President/Secretary | 2024-01-04 07:19 | 2024-01-10 03:04 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342996 | 21-000-601202 | BRENTWOOD GAS & MORE | 90615466 | Corte Madera Gas | 700 Tamalpais Drive | Corte Madera | 94925 | Confirmed/Updated Information | 1 | 10342996-001 | XERXES | A Stand-alone Tank | 15000 | 1999-03-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | Single-walled | Fiberglass |  | None |  | Fiberglass |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Rajinder Brar | President/Secretary | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 407 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | 208 | Yes | Yes | Yes | FE PETRO | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | No | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | EPA Guide: Managing Hazardous Waste. EPA Guide: Must for USTs. | Yes |  | Sukhwinder Singh | Facility Operator |  |  | Tank Owner/Operator |  | Rajinder Brar | President/Secretary | 2024-01-04 07:19 | 2024-01-10 03:04 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10342999 | 21-000-601571 | Elite Gas & Mart 1 | 90860245 | Mobil | 34 Ritter Street | San Rafael | 94901 | Renewal Permit | 3 | 10342999-003 | unknown | A Stand-alone Tank | 12000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | LISA THOMPSON | COMPLIANCE MANAGER | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | VEEDER ROOT | TLS-350 | VEEDER ROOT | MAG | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS 350 | VEEDER ROOT | 208 | Yes | Yes | Yes | RED JACKET | FXIVD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | FILL SUMP DIRECT BURY | LISA THOMPSON | COMPLIANCE MANAGER | DELONG LIU | DEALER | Authorized Representative of Owner |  | LISA THOMPSON | COMPLIANCE MANAGER | 2024-05-15 12:51 | 2024-05-15 13:17 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342999 | 21-000-601571 | Elite Gas & Mart 1 | 90860245 | Mobil | 34 Ritter Street | San Rafael | 94901 | Renewal Permit | 1 | 10342999-001 | unknown | A Stand-alone Tank | 12000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | LISA THOMPSON | COMPLIANCE MANAGER | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | VEEDER ROOT | TLS-350 | VEEDER ROOT | MAG | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS 350 | VEEDER ROOT | 208 | Yes | Yes | Yes | FE PETRO |  | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | FILL SUMP DIRECT BURY | LISA THOMPSON | COMPLIANCE MANAGER | Delong Liu | Dealer | Authorized Representative of Owner |  | LISA THOMPSON | COMPLIANCE MANAGER | 2024-05-15 12:51 | 2024-05-15 13:17 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10342999 | 21-000-601571 | Elite Gas & Mart 1 | 90860245 | Mobil | 34 Ritter Street | San Rafael | 94901 | Renewal Permit | 2 | 10342999-002 | unknown | A Stand-alone Tank | 12000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | LISA THOMPSON | COMPLIANCE MANAGER | Annually |  | Site Plan Previously Submitted | No | [5 empty] | Yes | VEEDER ROOT | TLS-350 | VEEDER ROOT | MAG | Continuous |  | 0.2 GPH |  | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TLS 350 | VEEDER ROOT | 208 | Yes | Yes | Yes | FE PETRO |  | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | FILL SUMP DIRECT BURY | LISA THOMPSON | COMPLIANCE MANAGER | DELONG LIU | DEALER | Authorized Representative of Owner |  | LISA THOMPSON | COMPLIANCE MANAGER | 2024-05-15 12:51 | 2024-05-15 13:17 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10343002 | 21-000-600974 | Sillada Union 76 #257384 | 90308782 | Sillada Union 76 #257384 | 1125 Lincoln Ave | San Rafael | 94901 | Confirmed/Updated Information | 2 | 10343002-002 | Modern Welding | A Stand-alone Tank | 12000 | 1991-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  |  | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | Sa-Ngasilpa Pungprakearti | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | VR-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | VR-208 | Yes | Yes | Yes | FE Petro | STP MCD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | [8 empty] | No |  | Arthur Pungprakearti | Owner | Patrick Pungprakearti | Owner | Facility Owner/Operator |  | Sa-Ngasilpa Pungprakearti | Owner | 2023-01-20 16:05 | 2023-03-28 15:37 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10343002 | 21-000-600974 | Sillada Union 76 #257384 | 90308782 | Sillada Union 76 #257384 | 1125 Lincoln Ave | San Rafael | 94901 | Confirmed/Updated Information | 1 | 10343002-001 | Modern Welding | A Stand-alone Tank | 12000 | 1991-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  |  | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Steel |  | No | No | Yes |  | Sa-Ngasilpa Pungprakearti | Owner | Annually |  | Site Plan Previously Submitted | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | VR-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS 350 | Veeder Root | VR-208 | Yes | Yes | Yes | FE Petro | STP MCD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | [8 empty] | No |  | Arthur Pungprakearti | Owner | Patrick Pungprakearti | Owner | Facility Owner/Operator |  | Sa-Ngasilpa Pungprakearti | Owner | 2023-01-20 16:05 | 2023-03-28 15:37 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA
10343047 | 21-000-601567 | AS Convenience & Energy Inc. | 90379039 | Terra Linda Gas | 1005 Northgate Drive | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10343047-001 | Trusco | A Stand-alone Tank | 12000 | 1999-12-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Robert Andrew Leuzinger | President/Owner | Annually |  | New Plan Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | VMI | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  | TLS-350 | Veeder-Root | 330212-001 | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel 'Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Robert Andrew Leuzinger | President/Owner | 2024-04-25 15:40 | 2024-05-09 11:03 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10343047 | 21-000-601567 | AS Convenience & Energy Inc. | 90379039 | Terra Linda Gas | 1005 Northgate Drive | San Rafael | 94903 | Confirmed/Updated Information | 2 | 10343047-002 | Trusco | A Stand-alone Tank | 8000 | 1999-12-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Flexible |  | Flexible |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | No | Single-walled | Fiberglass |  | No | No | Yes |  | Robert Andrew Leuzinger | President/Owner | Annually |  | New Plan Submitted | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder-Root | TLS-350 | Veeder-Root | 794380-208 | Yes | Yes | Yes | VMI | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Electronic Stand-alone |  |  | TLS-350 | Veeder-Root | 330212-001 | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel 'Sammy" Spencer | Regional Manager | Tank Owner/Operator |  | Robert Andrew Leuzinger | President/Owner | 2024-04-25 15:40 | 2024-05-09 11:03 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10343053 | 21-000-600996 | Mill Valley Gas & Mart | 90694231 | Mill Valley Gas & Mart | 630 Blithedale Avenue East | Mill Valley | 94941 | UST Removal | 1 | 10343053-001 | Owens | A Stand-alone Tank | 10000 | 1979-01-01 | 2014-03-20 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Continuous; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: No; Recordkeeping 490-68a: No; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: No; Training 490-70: No; Personnel Responsibilities 490-72: Mo Mashhoon; Personnel Responsibilities 490-73: President | 2017-06-26 10:23 | 2017-06-26 10:35 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343053 | 21-000-600996 | Mill Valley Gas & Mart | 90694231 | Mill Valley Gas & Mart | 630 Blithedale Avenue East | Mill Valley | 94941 | UST Removal | 2 | 10343053-002 | Owens | A Stand-alone Tank | 6000 | 1979-01-01 | 2014-03-20 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Continuous; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: No; Recordkeeping 490-68a: No; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: No; Training 490-70: No; Personnel Responsibilities 490-72: Mo Mashhoon; Personnel Responsibilities 490-73: President | 2017-06-26 10:23 | 2017-06-26 10:35 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343053 | 21-000-600996 | Mill Valley Gas & Mart | 90694231 | Mill Valley Gas & Mart | 630 Blithedale Avenue East | Mill Valley | 94941 | UST Removal | 3 | 10343053-003 | Owens | A Stand-alone Tank | 10000 | 1979-01-01 | 2014-03-20 |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Single Wall | Fiberglass |  | None |  | Yes | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: Single-walled; Under Dispenser Containment (UDC) 469b: Steel; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: Continuous; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: No; Recordkeeping 490-68a: No; Recordkeeping 490-68b: No; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: No; Training 490-70: No; Personnel Responsibilities 490-72: Mo Mashhoon; Personnel Responsibilities 490-73: President | 2017-06-26 10:23 | 2017-06-26 10:35 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343068 | 21-000-601069 | Salkhi | 90388270 | Fairfax Gas | 2001 Sir Francis Drake Boulevard | Fairfax | 94930 | UST Removal | 002 | 10343068-002 | unknown | A Stand-alone Tank | 10000 | 1899-12-31 | 2015-01-09 |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-350 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | [8 empty] | Yes |  | Arash Salkhi | President | Brittney De La Garza | District Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2017-06-05 16:25 | 2017-06-12 08:08 | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10343068 | 21-000-601069 | Salkhi | 90388270 | Fairfax Gas | 2001 Sir Francis Drake Boulevard | Fairfax | 94930 | UST Removal | 001 | 10343068-001 | unknown | A Stand-alone Tank | 10000 | 1899-12-31 | 2015-01-09 |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-350 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | [8 empty] | Yes |  | Arash Salkhi | President | Brittney De La Garza | District Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2017-06-05 16:25 | 2017-06-12 08:08 | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10343068 | 21-000-601069 | Salkhi | 90388270 | Fairfax Gas | 2001 Sir Francis Drake Boulevard | Fairfax | 94930 | UST Removal | 003 | 10343068-003 | unknown | A Stand-alone Tank | 8000 | 1899-12-31 | 2015-01-09 |  | 1 |  | Motor Vehicle Fueling |  | Midgrade Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Arash Salkhi | President | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-350 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly | [5 empty] | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | [8 empty] | Yes |  | Arash Salkhi | President | Brittney De La Garza | District Manager | Tank Owner/Operator |  | Arash Salkhi | President | 2017-06-05 16:25 | 2017-06-12 08:08 | Nadira Alicusic | Marin County Dept of Public Works CUPA | CUPA
10343089 | 21-000-601158 | Apro LLC | 90161914 | United # 5662 | 100 Marinwood Avenue | San Rafael | 94903 | Confirmed/Updated Information | 3 | 10343089-003 | Xerxes | A Stand-alone Tank | 12000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Allen Faass | Compliance | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Tom Robins | Staff Geologist | Stephanie Ferguson | Compliance Manager | Authorized Representative of Owner |  | Allen Faass | Compliance | 2024-01-18 12:39 | 2024-04-09 17:01 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343089 | 21-000-601158 | Apro LLC | 90161914 | United # 5662 | 100 Marinwood Avenue | San Rafael | 94903 | Confirmed/Updated Information | 4 | 10343089-004 | Xerxes | A Stand-alone Tank | 500 | 1899-12-31 |  |  | 1 |  | Hazardous Waste (includes used oil) |  | Used Oil |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Other | Gravity | [5 empty] | None |  | None |  | Single-walled | None |  | None |  | Steel |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Allen Faass; UST Tank Certification / Applicant Information 472: Compliance; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: Veeder Root; Continuous Electronic Tank Monitoring 490-8: TLS-350; Continuous Electronic Tank Monitoring 490-9: Veeder Root; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: Veeder Root; Continuous Monitoring of Piping Secondary Containment 490-31: TLS-350; Continuous Monitoring of Piping Secondary Containment 490-32: High Level; Continuous Monitoring of Piping Secondary Containment 490-33: ULS; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: No; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Tom Robins; Personnel Responsibilities 490-73: Staff Geologist; Personnel Responsibilities 490-74: Stephanie Ferguson; Personnel Responsibilities 490-75: Compliance Manager; UST Monitoring Plan Certification / Applicant Information 490-76: Authorized Representative of Owner; UST Monitoring Plan Certification / Applicant Information 490-78: Allen Faass; UST Monitoring Plan Certification / Applicant Information 490-79: Compliance | 2024-01-18 12:39 | 2024-04-09 17:01 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343089 | 21-000-601158 | Apro LLC | 90161914 | United # 5662 | 100 Marinwood Avenue | San Rafael | 94903 | Confirmed/Updated Information | 1 | 10343089-001 | Xerxes | A Stand-alone Tank | 12000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Allen Faass | Compliance | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Tom Robins | Staff Geologist | Stephanie Ferguson | Compliance Manager | Authorized Representative of Owner |  | Allen Faass | Compliance | 2024-01-18 12:39 | 2024-04-09 17:01 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10343089 | 21-000-601158 | Apro LLC | 90161914 | United # 5662 | 100 Marinwood Avenue | San Rafael | 94903 | Confirmed/Updated Information | 2 | 10343089-002 | Xerxes | A Stand-alone Tank | 12000 | 1899-12-31 |  |  | 1 |  | Motor Vehicle Fueling |  | Midgrade Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | None |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Allen Faass | Compliance | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 409 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | No |  |  | Yes | Veeder Root | PLLD |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 208 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | [8 empty] | Yes |  | Tom Robins | Staff Geologist | Stephanie Ferguson | Compliance Manager | Authorized Representative of Owner |  | Allen Faass | Compliance | 2024-01-18 12:39 | 2024-04-09 17:01 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10460464 | 21-000-600116 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 94737/1570 | 90 Madera Blvd | Corte Madera | 94925 | Confirmed/Updated Information | 3 | 10460464-003 | XERXES | A Stand-alone Tank | 8000 | 2007-07-19 |  |  | 1 | T3-DIESEL (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE | RETAIL HES | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 330020-463 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 330020-463 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-463 VACUUM SENSORS & VR-209 LIQUID SENSORS. VENT & UDC SUMPS MONITORED BY VR-463 VACUUM SENSORS & VR-208 LIQUID SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | CHARLES BITTLE | RETAIL HES | 2024-04-29 14:39 | 2024-05-13 19:05 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10460464 | 21-000-600116 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 94737/1570 | 90 Madera Blvd | Corte Madera | 94925 | Confirmed/Updated Information | 1 | 10460464-001 | XERXES | A Stand-alone Tank | 15000 | 2007-07-19 |  |  | 1 | T1-SUPREME (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE | RETAIL HES | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 330020-463 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 330020-463 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-463 VACUUM SENSORS & VR-209 LIQUID SENSORS. VENT & UDC SUMPS MONITORED BY VR-463 VACUUM SENSORS & VR-208 LIQUID SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | CHARLES BITTLE | RETAIL HES | 2024-04-29 14:39 | 2024-05-13 19:05 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10460464 | 21-000-600116 | Chevron Products Company (A Division of Chevron U.S.A. Inc.) | 90196153 | CHEVRON STATION# 94737/1570 | 90 Madera Blvd | Corte Madera | 94925 | Confirmed/Updated Information | 2 | 10460464-002 | XERXES | A Stand-alone Tank | 20000 | 2007-07-19 |  |  | 1 | T2-REGULAR (PER VEEDER-ROOT PROGRAMMING) | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | CHARLES BITTLE | RETAIL HES | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 330020-463 & 794380-209 | Yes | Yes | No |  |  | Yes | VEEDER-ROOT | PLLD Series 848480 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER-ROOT | TLS-350 PLUS | VEEDER-ROOT | 330020-463 & 794380-208 | Yes | Yes | Yes | No | Double-walled | Vacuum | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [8 empty] | Yes | UST TURBINE (STP) & FILL SUMPS MONITORED BY VR-463 VACUUM SENSORS & VR-209 LIQUID SENSORS. VENT & UDC SUMPS MONITORED BY VR-463 VACUUM SENSORS & VR-208 LIQUID SENSORS. ATG SYSTEM WITH IN-TANK VR-MAG PROBE FOR INVENTORY ONLY. OVERFILL PREVENTION METHOD: FILL TUBE SHUT OFF VALVE (FLAPPER). EVR ISD. | STATION MANAGER | STATION MANAGER | ASST. MANAGER | ASST. MANAGER | Tank Owner/Operator |  | CHARLES BITTLE | RETAIL HES | 2024-04-29 14:39 | 2024-05-13 19:05 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10473877 | 21-000-600098 | CDCR - California State Prison | 90102631 | CDCR - California State Prison San Quentin | 1 Main St | San Quentin | 94964 | Confirmed/Updated Information | GARAGE #2 | 10473877-002 | K & T STEEL CORP | A Stand-alone Tank | 4000 | 1990-12-04 |  |  | 1 | DIESEL | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Steel |  | None |  | None |  | None |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | Yes |  | RON DAVIS | WARDEN | Annually |  | Site Plan Previously Submitted | Yes | Dry | VEEDER ROOT | TSL 350 PLUS | VEEDER ROOT | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TSL 350 PLUS | VEEDER ROOT | 208 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | VEEDER ROOT | TLS 350 PLUS | BEAUDREAU | 404-4 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | [8 empty] | Yes |  | RON DAVIS | WARDEN | ADAM FREDLINE | ASSOC HAZARDOUS MATERIAL SPEC | Tank Owner/Operator |  | RON DAVIS | WARDEN | 2024-03-28 13:36 | 2024-06-10 13:48 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10473877 | 21-000-600098 | CDCR - California State Prison | 90102631 | CDCR - California State Prison San Quentin | 1 Main St | San Quentin | 94964 | Renewal Permit | GARAGE #1 | 10473877-001 | K & T STEEL CORP | A Stand-alone Tank | 10000 | 1990-12-04 |  |  | 1 | UNLEADED TANK AT GARAGE | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | Fiberglass |  | None | Steel |  | None |  | None |  | None |  | Yes | Yes | Yes | Single-walled | Steel |  | No | No | Yes |  | RON DAVIS | WARDEN | Annually |  | Site Plan Previously Submitted | Yes | Dry | VEEDER ROOT | TSL 350 PLUS | VEEDER ROOT | 420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | VEEDER ROOT | TSL 350 PLUS | VEEDER ROOT | 208 | Yes | Yes | No |  |  | No | [5 empty] | No |  |  | No |  | Yes | No | No |  | Continuous |  | VEEDER ROOT | TLS 350 PLUS | BEAUDREAU | 404-4 | Yes | Yes | Yes | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | [8 empty] | Yes |  | RON DAVIS | WARDEN | ADAM FREDLINE | ASSOC HAZARDOUS MATERIAL SPEC | Tank Owner/Operator |  | RON DAVIS | WARDEN | 2024-03-28 13:36 | 2024-06-10 13:48 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10473877 | 21-000-600098 | CDCR - California State Prison | 90102631 | CDCR - California State Prison San Quentin | 1 Main St | San Quentin | 94964 | Confirmed/Updated Information | EMERGENCY GEN #3 | 10473877-003 | UNKNOWN | A Stand-alone Tank | 6000 | 1998-01-01 |  |  | 1 | DIESEL | Emergency Generator Fuel |  | Diesel |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | 23 CCR §2636(a)(3) Suction | Fiberglass |  | Fiberglass |  | Single-walled | Steel |  | None |  | None | None |  | None |  | None |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: Yes; Fill Components Installed 451-c: Yes; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: RON DAVIS; UST Tank Certification / Applicant Information 472: WARDEN; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: Yes; Continuous Electronic Tank Monitoring 490-6: Dry; Continuous Electronic Tank Monitoring 490-7: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-8: 250 GILBARCO; Continuous Electronic Tank Monitoring 490-9: VEEDER ROOT; Continuous Electronic Tank Monitoring 490-10: 420; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: Yes; Continuous Monitoring of Piping Secondary Containment 490-29: Dry; Continuous Monitoring of Piping Secondary Containment 490-30: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-31: 250 GILBARCO; Continuous Monitoring of Piping Secondary Containment 490-32: VEEDER ROOT; Continuous Monitoring of Piping Secondary Containment 490-33: 208; Continuous Monitoring of Piping Secondary Containment 490-34: No; Continuous Monitoring of Piping Secondary Containment 490-35: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: Yes; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Under Dispenser Containment (UDC) Monitoring 490-59: No; Under Dispenser Containment (UDC) Monitoring 490-60: No; Under Dispenser Containment (UDC) Monitoring 490-61: No; Under Dispenser Containment (UDC) Monitoring 490-62: No; Periodic System Testing 490-65: No; Periodic System Testing 490-66: Yes; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: Yes; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: RON DAVIS; Personnel Responsibilities 490-73: WARDEN; Personnel Responsibilities 490-74: ADAM FREDLINE; Personnel Responsibilities 490-75: ASSOC HAZARDOUS MATERIAL SPEC; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: RON DAVIS; UST Monitoring Plan Certification / Applicant Information 490-79: WARDEN | 2024-03-28 13:36 | 2024-06-10 13:48 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10483969 | 21-000-600060 | Novato 76 | 90410779 | Novato 76 | 375 Ignacio Blvd | Novato | 94949 | Confirmed/Updated Information | 1 | 10483969-001 | Modern Welding | A Stand-alone Tank | 15000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Ali M. Mahmoodi | Owner | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | Vaporless | LD2000 | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly |  | n/a | n/a | Mechanical | Float & Chain | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Dispenser's 1,2,5,6,7,8,9,10 are Mechanical Ball & Float. Dispenser's 3,4,11 and 12 are Veeder Root 794380-208. | Ali M. Mahmoodi | Owner | Tony Bhangoo | Manager | Tank Owner/Operator |  | Ali M. Mahmoodi | Owner | 2023-01-11 13:28 | 2023-04-10 12:57 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10483969 | 21-000-600060 | Novato 76 | 90410779 | Novato 76 | 375 Ignacio Blvd | Novato | 94949 | Confirmed/Updated Information | 3 | 10483969-003 | Xerxes | A Stand-alone Tank | 10000 | 2012-12-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | None |  | None | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  | Ali M. Mahmoodi | Owner | Annually |  | New Plan Submitted | Yes | Liquid-Filled | Veeder Root | TLS-350 | Veeder Root | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | Veeder Root | TLS-350 | Veeder Root | 794380-208 / 332175-001 | Yes | Yes | No |  |  | Yes | Veeder Root | 848480-001 | 0.2 GPH | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | Veeder Root | TLS-350 | Veeder Root | 794380-208/304 | Yes | Yes | Yes | Yes | Double-walled | Liquid | Yes | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Dispenser's 1,2,5,6,7,8,9,10 are Mechanical Ball & Float. Dispenser's 3,4,11 and 12 are Veeder Root 794380-208. | Ali M. Mahmoodi | Owner | Tony Bhangoo | Manager | Tank Owner/Operator |  | Ali M. Mahmoodi | Owner | 2023-01-11 13:28 | 2023-04-10 12:57 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10483969 | 21-000-600060 | Novato 76 | 90410779 | Novato 76 | 375 Ignacio Blvd | Novato | 94949 | Confirmed/Updated Information | 2 | 10483969-002 | Modern Welding | A Stand-alone Tank | 15000 | 1995-01-01 |  |  | 1 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Steel |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Single-walled | Fiberglass |  | None |  | None | Fiberglass |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Single-walled | Fiberglass |  | No | No | Yes |  | Ali M. Mahmoodi | Owner | Annually |  | New Plan Submitted | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-420 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Dry | Veeder Root | TLS-350 | Veeder Root | 794380-208 | Yes | Yes | Yes | FE Petro | STP-MLD | No | [5 empty] | No |  |  | No |  | No | No | No |  | Float and Chain Assembly |  | n/a | n/a | Mechanical | Float & Chain | No | No | No | Yes | Single-walled |  |  | No | Yes | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manuals | Yes | Dispenser's 1,2,5,6,7,8,9,10 are Mechanical Ball & Float. Dispenser's 3,4,11 and 12 are Veeder Root 794380-208. | Ali M. Mahmoodi | Owner | Tony Bhangoo | Manager | Tank Owner/Operator |  | Ali M. Mahmoodi | Owner | 2023-01-11 13:28 | 2023-04-10 12:57 | Michael Faryna | Marin County Dept of Public Works CUPA | CUPA
10500199 | 21-000-600234 | Sewerage Agency of Southern Marin | 90104014 | Sewerage Agency of Southern Marin - Ricardo Rd PS | 10 Seminary Dr | Mill Valley | 94941 | UST Removal | 1 | 10500199-001 | Owens Corning | A Stand-alone Tank | 550 | 1982-01-01 | 2019-09-05 |  | 1 |  | Emergency Generator Fuel |  | Diesel |  |  | Single Wall | Fiberglass |  | None |  | No | No | Yes | No | Single-walled | Conventional Suction | Flexible |  | None |  | None | Steel |  | None |  | None | None |  | None |  | Fiberglass |  | None |  | Fill Components Installed 451-a: Yes; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: Yes; Corrosion Prevention 448b: No; Corrosion Prevention 448c: Yes; UST Tank Certification / Applicant Information 471: Chris Monti; UST Tank Certification / Applicant Information 472: CPO; Equipment Testing and Preventive Maintenance 490-3a: Annually; Site Plot Plan Submitted 490-4: Site Plan Previously Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: Yes; Tank Integrity Testing 490-23: Yes; Tank Integrity Testing 490-24: Annually; Other Tank Monitoring 490-26: No; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: Yes; Pipeline Integrity Testing 490-46: Every 3 Years; Visual Pipeline Monitoring 490-48: Yes; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: No; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: Yes; Recordkeeping 490-68a: No; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: Yes; Recordkeeping 490-68d: Yes; Recordkeeping 490-68e: Yes; Recordkeeping 490-68f: No; Recordkeeping 490-68g: Yes; Recordkeeping 490-68h: Yes; Training 490-69a: Yes; Training 490-70: Yes; Personnel Responsibilities 490-72: Mark Grushayev; Personnel Responsibilities 490-73: Wastewater Treatment Manager; Personnel Responsibilities 490-74: Chris Monti; Personnel Responsibilities 490-75: Operations Supervisor; UST Monitoring Plan Certification / Applicant Information 490-76: Tank Owner/Operator; UST Monitoring Plan Certification / Applicant Information 490-78: Mark Grushayev; UST Monitoring Plan Certification / Applicant Information 490-79: Wastewater Treatment Manager | 2019-11-22 12:32 | 2019-11-22 13:29 | Christie Coleman | Marin County Dept of Public Works CUPA | CUPA
10810900 | 21-000-601315 | AS Convenience & Energy Inc. | 90379039 | 24/7 Kentfield | 2066 Redwood Hwy | Greenbrae | 94939 | Confirmed/Updated Information | 3 | 10810900-003 | Xerxes | One in a Compartmented Unit | 7000 | 2019-07-12 |  |  | 2 |  | Motor Vehicle Fueling |  | Diesel |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | None |  | None |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Liquid | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304/ 330020-480 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager |  |  |  |  | 2024-07-11 10:10 | 2024-07-11 14:22 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10810900 | 21-000-601315 | AS Convenience & Energy Inc. | 90379039 | 24/7 Kentfield | 2066 Redwood Hwy | Greenbrae | 94939 | Confirmed/Updated Information | 1 | 10810900-001 | Xerxes | A Stand-alone Tank | 15000 | 2019-07-12 |  |  | 1 |  | Motor Vehicle Fueling |  | Regular Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304/330020-485 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager |  |  |  |  | 2024-07-11 10:10 | 2024-07-11 14:22 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10810900 | 21-000-601315 | AS Convenience & Energy Inc. | 90379039 | 24/7 Kentfield | 2066 Redwood Hwy | Greenbrae | 94939 | Confirmed/Updated Information | 2 | 10810900-002 | Xerxes | One in a Compartmented Unit | 8000 | 2019-04-12 |  |  | 2 |  | Motor Vehicle Fueling |  | Premium Unleaded |  |  | Double Wall | Fiberglass |  | Fiberglass |  | No | No | Yes | No | Double-walled | Pressure | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Double-walled | Fiberglass |  | Fiberglass |  | Steel |  | Fiberglass |  | Yes | Yes | Yes | Double-walled | Fiberglass |  | No | No | Yes |  |  |  | Annually |  | New Plan Submitted | Yes | Liquid-Filled | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-303 | No | [8 empty] | No | No |  | No |  |  | No |  | Yes | Under Vacuum | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304/330020-480 | Yes | Yes | No |  |  | Yes | VEEDER ROOT | 8484 |  | Yes | Yes | No |  |  | No |  | No | No | No |  | Continuous |  | VEEDER ROOT | TLS-350 | VEEDER ROOT | 794380-208/794380-304 | Yes | Yes | Yes | No | Double-walled | Liquid | Yes | No | No | Yes | Yes | Yes | No | No | No | No | No | Yes | Yes | [7 empty] | UST Monitoring Plan, Operating Manual | Yes |  | Arash Salkhi | President | Samuel "Sammy" Spencer | Regional Manager |  |  |  |  | 2024-07-11 10:10 | 2024-07-11 14:22 | Chris Rundell | Marin County Dept of Public Works CUPA | CUPA
10957150 |  | County of Marin | 90404194 | County of Marin/BB2 Site | 636 Sir Francis Drake Blvd | San Anselmo | 94960 | New Permit | BB2 | 10957150-001 | Unknown | A Stand-alone Tank | 125 |  |  | 2024-03-04 | 1 |  | Unknown |  | Other Non-petroleum |  | Unknown | Unknown | Unknown |  | Unknown |  | No | No | No | No | Other | Gravity | Unknown |  | Unknown |  | None | None |  | None |  | None | None |  | None |  | None |  | None |  | Fill Components Installed 451-a: No; Fill Components Installed 451-b: No; Fill Components Installed 451-c: No; Under Dispenser Containment (UDC) 469a: No Dispensers; Under Dispenser Containment (UDC) 469b: None; Corrosion Prevention 448a: No; Corrosion Prevention 448b: No; Corrosion Prevention 448c: No; Equipment Testing and Preventive Maintenance 490-3a: Other; Equipment Testing and Preventive Maintenance 490-3b: N/A; Site Plot Plan Submitted 490-4: New Plan Submitted; Continuous Electronic Tank Monitoring 490-5: No; Automatic Tank Gauging 490-11: No; Monthly Statistical Inventory Reconciliation 490-20: No; Weekly Manual Tank Gauge 490-21: No; Tank Integrity Testing 490-23: No; Other Tank Monitoring 490-26: Yes; Continuous Monitoring of Piping Secondary Containment 490-28: No; Mechanical Line Leak Detector Performs 3 GPH Leak Test 490-36: No; Electronic Line Leak Detector Performs 3 GPH Leak Test 490-39: No; Pipeline Integrity Testing 490-45: No; Visual Pipeline Monitoring 490-48: No; Suction Piping Meets Exemption Criteria 490-50: No; No Regulated Piping Per Health and Safety Code, Division 20, Chapter 6.7 Is Connected To The Tank System 490-51: Yes; Other Pipeline Monitoring 490-52: No; Under Dispenser Containment (UDC) Monitoring 490-54a: No Dispensers; Periodic System Testing 490-65: No; Periodic System Testing 490-66: No; Periodic System Testing 490-67: No; Recordkeeping 490-68a: No; Recordkeeping 490-68b: Yes; Recordkeeping 490-68c: No; Recordkeeping 490-68d: No; Recordkeeping 490-68e: No; Recordkeeping 490-68f: No; Recordkeeping 490-68g: No; Recordkeeping 490-68h: No; Training 490-69a: Yes; Training 490-70: Yes; Comments and Additional Information 490-71: Tank is abandoned in place with no continuous monitoring. Tank to be removed in future.; Personnel Responsibilities 490-72: Joanna Dixon; Personnel Responsibilities 490-73: Civil Engineer; Personnel Responsibilities 490-74: Tracy Clay; Personnel Responsibilities 490-75: Principal Civil Engineer | 2024-06-06 15:56 | 2024-06-11 08:42 | Julia Barnes | Marin County Dept of Public Works CUPA | CUPA

## UST Cert of Installation & Mod
Facility Identification and Location | [5 empty] | UST Certification Project Type |  |  |  |  | Work Authorized Under Permit |  | Contractor Information |  |  | Certification / Applicant Information | [5 empty] | Submittal / Acceptance Information |  |  | Regulator Information
1a | 1 | 3 | 103 | 104 |  | 483a-1 | 483a-2 | 483a-3 | 483a-4 | 483a-5 | 483b | 483c | 482a | 482b | 482c | 484 | 485 | 486 | 487 | 488 | 489
CERS ID | Facility ID | Facility Name | Facility Street Address | Facility City | Facility ZIP Code | Tank Installation / Replacement | Piping Installation / Replacement | Sump Installation / Replacement | Under Dispenser Containment Installation / Replacement | Other | Work Authorized Under Permit (Number or Date) | Description of Work Being Certified | Name of Contractor Who Performed Installation/ Modification | Contractor's License Number | Contractor's ICC Certification Number | Date Certified | Certifier’s Name | Certifier’s Title | Phone Number | Name of Certifier’s Employer | Certifier’s Relationship to Tank Owner | Date Submitted to CERS | Date Accepted by Regulator | Regulator Agent Name | Regulator Name | Regulator Type